## Sheet1
CIR/ FSR Number	Turbine	Customer	SiteName	FnLoc	Capacity	Tower Height	Blade	Generator	GR Slno	GearBox	GBSlno	Temprature	Dust	Corrosion	DOC	WONumber	DateOfFailure	Alarmcode	Employee	SwVersion	FwVersion	WTGStartTime	WTGStopTime	Production	RunHrs	FuncSystem	ComponentGroup	PartCode	ComponentMake	FailureDuring	SerialNumber	ProblemDesc	What	When	Where	Why	Who	How To Do	How Much	Consequence	Status	Action Performed	Comments	Files
CIR-10000239	100260057	Sudhan Spinning Mills (P) Ltd	ELAVANTHI	WF-IN-022-0833-Y2-A-008	0.85	65	Standard	Indar	20305001085	Rexroth	72802009277	High Temperature	STD+	Standard	29/03/2010			210-Brake drive error	Mylsamy P.	0	0	01/01/1900 00:00:00	01/01/1900 00:00:00	0	0	MECHANICAL	BLADES			LIGHTNING		TESTING	TEST ENTRY	TEST ENTRY	TEST ENTRY	TEST ENTRY	TEST ENTRY	TEST ENTRY	TEST ENTRY	TEST ENTRY	Closed	TEST ENTRY	TEST ENTRY BY FE-Field Engineer-Mylsamy P. | TEST ENTRY BY FOM-Field Operations Manager-Dhanabal S | TEST ENTRY BY PTS-Phone Technical Support-Senthil M. | TEST ENTRY BY FSL-Functionality Support Lead-Jayaprakash J. | TEST ENTRY BY FSS-Functionality Support Specialist-Babu M. | TEST ENTRY BY QUALITY-Quality-Vijay Chinnaswamy
CIR-10000268	100260057	Sudhan Spinning Mills (P) Ltd	ELAVANTHI	WF-IN-022-0833-Y2-A-008	0.85	65	Standard	Indar	20305001085	Rexroth	72802009277	High Temperature	STD+	Standard	29/03/2010		11/04/2016	111-Max hydraulic unit pumping time	Jeno V	0	0	11/04/2016 15:08:29	11/04/2016 15:08:29	0	0	ELECTRICAL	BLADES			LIGHTNING		dfsdf									Assigned	sdfsdf	fsdfsdfsd-Field Engineer-Jeno V | THE USER NOT IN OUR TEAM-Field Operations Manager-Dhanabal S | FSL Comments Requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Anand A.P
CIR-10000269	100260057	Sudhan Spinning Mills (P) Ltd	ELAVANTHI	WF-IN-022-0833-Y2-A-008	0.85	65	Standard	Indar	20305001085	Rexroth	72802009277	High Temperature	STD+	Standard	29/03/2010		11/04/2016	-0	Jeno V	0	0	11/04/2016 15:08:29	11/04/2016 15:08:29	0	0	CONTROL SYSTEM	BEACON SYSTEM			GRID FAILURE		gfdfdf									Deleted	dfgdfgdf
CIR-10000195	G9011	Maple Renewable Power Pvt Ltd	PIONEER - TIRUNELVELI	WF-IN-022-0079-Y1-A-013	0.85							High Temperature	STD+	Standard	04/05/2007		26/03/2016	-0	Mervyn Tilak M.	1404	1440	26/03/2016 15:30:00	26/03/2016 10:30:00	0	0	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	880162		NORMAL OPERATION		203- Low hydraulic unit pressure	Low hydraulic unit pressure	normal operation time	Hydraulic unit	hyd pressure suddenly reduced	T. Linga Murugan	During inspection time we check the hydraulic related circuits at that time we found the proportional valve was failed.	5 hrs	Proportional valve replaced	Assigned	During inspection time we check the hydraulic related circuits at that time we found the proportional valve was failed.	Proportional valve replaced-Field Engineer-Mervyn Tilak M. | Failure proportional valve replaced-Field Operations Manager-Dhanabalan I. | Accumulator pre charge pressure and Oil purity to be checked , If required please change the Hydraulic oil filter-Phone Technical Support-Senthil M. | Please ensure if you have implemented filter for proprtional valve (B5041203).-Functionality Support Lead-Anand A.P | Ok, please pass this to Design modification team-Quality-Vijay Chinnaswamy | Please check this Issue-Functionality Support Lead-Shankar Anand R. | -Functionality Support Specialist-Babu M.	IMG-20160329-WA0018.jpg | B5021301 10_04_2013 R0_G5X _EN.pdf
CIR-10000194	G7193	Pioneer Overseas Private Ltd	PIONEER - TIRUNELVELI	WF-IN-022-0079-Y1-A-028	0.85							High Temperature	STD+	Standard	28/05/2005		24/03/2016	-0	Dhanabalan I.	0	1440	26/03/2016 15:00:00	24/03/2016 11:00:00	0	0	MECHANICAL	YAW SYSTEM	P430140	Briveni	NORMAL OPERATION		107 Rotor motor thermal	Rotor motor thermal	during running(yawing) time	Nacelle Panel side yaw gear unit	Due to agening & Continous operation	S. Justin Vimal Raj, S. Arun Prasad,T. Linga Murugan, M. Maharaja	During inspection time we found checked yaw motor related connection electrically found ok. So we manually on the MPCB and we yaw the WTG at that time we heared the humming sound from the motor and again MPCB was tripped then we check the yaw gear unit at that time we found panel side yaw gear unit was failed.	55 hrs	Yaw gear unit replaced	Closed	During inspection time we found checked yaw motor related connection electrically found ok. So we manually on the MPCB and we yaw the WTG at that time we heared the humming sound from the motor and again MPCB was tripped then we check the yaw gear unit at that time we found panel side yaw gear unit was failed.	Panel side yaw gear unit replaced-Field Engineer-Mervyn Tilak M. | Failure yaw gear unit replaced-Field Operations Manager-Dhanabalan I. | Further investigation recommanded-Phone Technical Support-Senthil M. | Yaw gear unit repalced-Functionality Support Lead-Hemkumar D | To be passed to repair circuit for analysis-Quality-Vijay Chinnaswamy	IMG-20160329-WA0004.jpg
CIR-10000724	100260726	Beta Wind Farm Private Limited	NAVALADI	WF-IN-022-1077-Y0-A-003	0.85	65	Standard	ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	30/03/2012		20/06/2016	-0	Mervyn Tilak M.	1404	1439	01/01/1900 00:00:00	20/06/2016 10:32:00	0	0	ELECTRICAL	GENERATOR SYSTEM	GP008207	Canatery	NORMAL OPERATION	447676	3233-Error in stator phase sequence	3233-Error in stator phase sequence	While normal running mode	nacelle	Surge voltage	Generator	During inspection time we checked the generator rotor and stator winding values are varied.		Now WTG is in stopped condition kindly advise us to proceed further.	Assigned	During inspection time we checked and found the generator rotor and stator winding values are varied.	Waiting for clearance or adivise-Field Engineer-Mervyn Tilak M. | Waiting for your instruction to proceed further-Field Operations Manager-Dhanabalan I. | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.	IMG-20160621-WA0009.jpg | IMG-20160621-WA0009.jpg | SF NO-549 Generator inspection sheet.xls
CIR-10000130	G8598	Maple Renewable Power Pvt Ltd	PIONEER - TIRUNELVELI	WF-IN-022-0079-Y1-A-006	0.85							High Temperature	STD+	Standard	30/03/2006		15/03/2016	-0	Mervyn Tilak M.	1404	1440	17/03/2016 16:00:00	17/03/2016 15:00:00	0	0	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP008132		GRID FAILURE		Error no 310 Turbine Preheating	Turbine Pre heating	Power resuming time	Multiplexer card	Surge Volatge	M. Mervyn Tilak, I. Dhanabalan	Check temperature in the display found not read, then we check multiplexer card and their related connections.	1hrs	Multiplexer card failed	Assigned	Check temperature in the display found not read, then we check multiplexer card and their related connections.	Multiplexer card failed-Field Engineer-Mervyn Tilak M. | Multiplexer card replaced-Field Operations Manager-Dhanabalan I. | solved-Phone Technical Support-Senthil M. | problem resolved-Functionality Support Lead-Shankar Anand R. | -Quality-Vijay Chinnaswamy	IMG_20160318_202546.jpg
CIR-10000255	G8598	Maple Renewable Power Pvt Ltd	PIONEER - TIRUNELVELI	WF-IN-022-0079-Y1-A-006	0.85							High Temperature	STD+	Standard	30/03/2006		04/04/2016	322-Anemometer error	Mervyn Tilak M.	1404	1440	04/04/2016 18:00:00	04/04/2016 15:00:00	0	0	CONTROL SYSTEM	NACELLE INSTRUMENTATION SYSTEM	9000601		NORMAL OPERATION		322-Anemometer error	322-Anemometer error	When the wind speed is below 5 m/s	At nacelle	Due to ageing & expose to atmosphere directly	S. Justin Vimal Raj, I. Jeba Kumar.	We physically checked the anemometer working condition, we found anemometer bearing was jammed due to this issue wind speed was not reading properly.	3 hrs		Assigned	We physically checked the anemometer working condition, we found anemometer bearing was jammed due to this issue wind speed was not reading properly.	Bearing jammed anemometer replaced by new one-Field Engineer-Mervyn Tilak M. | Anemometer replaced-Field Operations Manager-Dhanabalan I. | closed-Phone Technical Support-Senthil M. | -Functionality Support Lead-Shankar Anand R.	20150721_182501.jpg
CIR-10000718	G8598	Maple Renewable Power Pvt Ltd	PIONEER - TIRUNELVELI	WF-IN-022-0079-Y1-A-006	0.85							High Temperature	STD+	Standard	30/03/2006		16/06/2016	-0	Mervyn Tilak M.	1404	1440	16/06/2016 14:00:00	16/06/2016 11:30:00	0	0	CONTROL SYSTEM	NACELLE INSTRUMENTATION SYSTEM	9000601	NRG anemometer	NORMAL OPERATION		302 High wind speed	302 High wind speed	While normal running mode	At nacelle	Surge voltage or due to agening	5002183	During inspection time we found wind speed seems to be more than m/s so we checked the anemometer related connections for any loose connection/ short circuit but every things are fine so we confirmed anemometer was failed. After replacing the failure component by new one WTG was restarted.	2.5 hrs	Anomometer replaced.	Applied	During inspection time we found wind speed seems to be more than m/s so we checked the anemometer related connections for any loose connection/ short circuit but every things are fine so we confirmed anemometer was failed. After replacing the failure component by new one WTG was restarted.	Anemometer failed-Field Engineer-Mervyn Tilak M. | -Field Operations Manager-Dhanabalan I.	20150721_182501.jpg
CIR-10000420	2006329509	Vayu Energy Private Ltd	PIONEER-TENKASI	WF-IN-022-0317-Y1-A-006	0.85	65	Standard	Indar	8507	Hansen	174.277	High Temperature	STD+	Standard	30/04/2013	402361102	12/05/2016	-0	Ebinezar Rajesh S.	1404	1440	12/05/2016 23:50:00	12/05/2016 20:00:00	4027418	18709.5	ELECTRICAL	ELECTRICAL CABINET SYSTEM	Gp012585 P390157 GP188019 GP207202 GP008132 GP0081	Team( Ingecon wind) Hubner berlin DEHNguard DEHNra	LIGHTNING	257642745 1926053 900681 nil 154863468 68854162 60947-1	Error no:700 PLC converter communication error.During heavy lightning in this error was occurred.	Error no:700 PLC converter communication error.	During heavy lightning in this error was occurred.	SF NO: 170 (In Bottom control panel electrical system)	heavy lightning,Voltage fluctuation,Short circuit,etc...	Mr.P.Lingaraja and Mr.V.Saravanakumar	Replaced by new spares.	GP012585-1No P390157-1No GP188019-1No GP207202-1No GP008132-1No GP008132-1No P393298-1No	After replaced by new spares,turbine running with normal operation.	Applied	During heavy lightning in this error no:700 PLC converter Comm error was occurred.We have checked and found that CCU was failure.So the CCU was changed by new one.At that time Encoder error not ok fault and Line protection triggered error was came.We checked and found Encoder,Multiplexer card,5A power supply unit, MPCB, 230v Dhen card and 690v Dhen card were failure condition.So we replaced by all spares by new.Now wtg running normal condition.	After replaced by new spares,turbine running with normal operation.-Field Engineer-Mangala Rajan A. | heavy lightning in this error was occurred.Issue closed-Field Operations Manager-Ebinezar Rajesh S. | Kindly provide the turbine id &windfarm name and Reassign the same-Phone Technical Support-Senthil M. | Turbine id & wind farm name was already provided.Please open the online CIR portal when internet access is full strength.-Field Engineer-Mangala Rajan A. | -Field Operations Manager-Ebinezar Rajesh S.	Ingeteam CCU.jpg CCU | Gen.Encoder.jpg Encoder | 20160517_141901.jpg MPCP | 20160517_141901.jpg MPCB | 20160517_142422.jpg Multiplexer card | 20160517_142229.jpg 5A Power supply unit | 20160518_111827.jpg 690Vac dhen card | 20160518_111740.jpg | 20160518_111740.jpg 230Vac dhen card | 20160518_111827.jpg 690 Vac Dehn card | 20160518_111740.jpg 230 Vac Dehn card
CIR-10000259	G8597	TVH Energy Resource Private Limited	PIONEER - TIRUNELVELI	WF-IN-022-0079-Y1-A-007	0.85							High Temperature	STD+	Standard	30/03/2006		07/04/2016	-0	Dhanabalan I.	1404	1440	07/04/2016 23:00:00	07/04/2016 13:00:00	0	0	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP012585	Ingeteam	NORMAL OPERATION	A6460004507		700 - PLC- Converter Comm Erro	Normal Operation	Bottom panel converter	Continuous operation	Justin & Jeba	During inspection time we checked the bottom panel converter section at that time we found CCU 88 status was not ok.	10hrs	CCU replaced	Assigned	During inspection time we checked the bottom panel converter section at that time we found CCU 88 status was not ok.	CCU replaced by new one.-Field Engineer-Mervyn Tilak M. | CCU replaced-Field Operations Manager-Dhanabalan I. | BOP Auditing to be done-Phone Technical Support-Senthil M. | Type I Surge Arrester recommended . This is under Top 20 component failure catagory list-Functionality Support Lead-Murugesan P. | -Quality-Vijay Chinnaswamy	IMG_20160215_112925.jpg
CIR-10000708	2006329509	Vayu Energy Private Ltd	PIONEER-TENKASI	WF-IN-022-0317-Y1-A-006	0.85	65	Standard	Indar	8507	Hansen	174.277	High Temperature	STD+	Standard	30/04/2013	402393341	13/06/2016	2118-Interbus bus error	Mangala Rajan A.	1404	1440	13/06/2016 09:30:00	13/06/2016 06:00:00	4307329	19285.25	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004890 GP004891 GP004892	Phonix Contact	NORMAL OPERATION	1110115239 1110073962 1110134690	Error No:2118-Inter bus bus error.When turbine running this error was occurred frequently.	Error No:2118-Inter bus bus error.	When turbine running this error was occurred frequently.	SF NO:170 (In top control panel bus system)	Continuous operation,Short circuit,loose connection and Material defect..	V.Saravana kumar and P.Lingaraja	Replaced by new spares.	GP004890 - 1No GP004891 - 1 No GP004892 - 1 No	After replaced by new spares turbine running with normal operation.	Applied	Wtg stopped due to error no:2118-Inter bus bus error. | When turbine running this error was occurred frequently. | We check the additional alarms in HMI Log and it's related connections and found DO16,SEG- ELF and ED1 Modules got internal failure. | So we replaced by new spares.	After replaced by new spares turbine running with normal operation.-Field Engineer-Mangala Rajan A. | -Field Operations Manager-Ebinezar Rajesh S.	Digital output.jpg IB IL 24 DO 16-PAC | Digital input.jpg ACC_PHO_IB IL 24 DI 8/T2-PAC_2862204 | SEG module.jpg ACC_PHO_IB IL 24 SEG ELF PAC_2861409
CIR-10000172	2006349517	Surana Corporation Ltd	PIONEER-TENKASI	WF-IN-022-0317-Y1-A-003	0.85	65	Standard	Indar	8504	Hansen	173.533	High Temperature	STD+	Standard	11/05/2013	402285945	01/03/2016	-0	Ebinezar Rajesh S.	1404	1440	01/03/2016 20:30:00	01/03/2016 17:00:00	4149928	16115.43	CONTROL SYSTEM	SOFTWARE	GP004975	PHONIX CONTACT	NORMAL OPERATION		Error no:2107 PLC Initialization Failure.When turbine running this error occoured.	Error no:2107 PLC Initialization Failure.	During Turbine Running this error occoured.	SF No:202/3 (SURANA 3)	PLC Failure	Mr.A.Mangala Rajan	Replaced by new PLC module(RFC 430 ETH-IB). .	1-No	After replaced the PLC module(RFC 430 ETH-IB) turbine running with normal operation.	Closed	During running time this error no:2107 Plc installation failure was occurred.We check and found Plc was failed.So we replaced by new one then program was upgraded.	After replaced the PLC module (RFC 430 ETH-IB) turbine running with normal operation.-Field Engineer-Lingaraja P. | replaced the PLC module(RFC 430 ETH-IB) Problem solved-Field Operations Manager-Ebinezar Rajesh S. | closed-Phone Technical Support-Senthil M. | Problem resolved-Functionality Support Lead-Shankar Anand R. | closed-Quality-Vijay Chinnaswamy	PLC.jpg
CIR-10000271	100260062	Vedha Spinning Mills (P) Ltd	ELAVANTHI	WF-IN-022-0833-Y1-A-001	0.85	65	Standard	Indar	20305001107	Gamesa(China)	601883	High Temperature	STD+	Standard	17/04/2010		11/04/2016	111-Max hydraulic unit pumping time	Jeno V	0	0	11/04/2016 16:32:00	11/04/2016 16:32:00	0	0	CONTROL SYSTEM	BEACON SYSTEM			GRID FAILURE		op									Deleted	op
CIR-10000533	100260062	Vedha Spinning Mills (P) Ltd	ELAVANTHI	WF-IN-022-0833-Y1-A-001	0.85	65	Standard	Indar	20305001107	Gamesa(China)	601883	High Temperature	STD+	Standard	17/04/2010	402366374	17/05/2016	-0	Yathavaraj V	1394	1437	17/05/2016 12:30:00	17/05/2016 22:10:00	8059160	46649	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP012585	INGETEAM	NORMAL OPERATION	AK9670*A6460004506*B	700 -PLC COVERTOR COMMUNICATION ERROR.	CCU FAILURE	DURING NORMAL OPERATION	BOTTOM CONTROL PANEL	GRID PROBLEM	CONVERTOR CONTROL UNIT	PROGRAME FLASH	01 NUMBER	WTG STOPPED DUE TO ERROR 700 -PLC. CONVERTOR COMM.FAIL. ON CHECKING THE ERROR, FOUND THAT CCU WAS IN ERROR MODE, THE ERROR CODE IS H1 AND CCU NOT CONNECTED TO LAPTOP, SO WE RESET THE CCU BY PRESSING OF RESET BUTTON IN CCU AND THEN RE-PROGRAM THE CCU FOUND OK THEN RESET THE WTG, DURING THAT TIME AGAIN CCU GOES TO ERROR MODE. HENCE FORTH WE CONFIRMED CCU WAS FAILURE. SO REPLACED THE CCU BY NEW ONE. THEN UPLOAD THE FIRMWARE AND CHECKED ERROR FREE FOUND OK. THERE AFTER WTG PUT BACK INTO OPERATION MO	Assigned	WTG STOPPED DUE TO ERROR 700 -PLC. CONVERTOR COMM.FAIL. ON CHECKING THE ERROR, FOUND THAT CCU WAS IN ERROR MODE, THE ERROR CODE IS H1 AND CCU NOT CONNECTED TO LAPTOP, SO WE RESET THE CCU BY PRESSING OF RESET BUTTON IN CCU AND THEN RE-PROGRAM THE CCU FOUND OK THEN RESET THE WTG, DURING THAT TIME AGAI	WTG STOPPED DUE TO ERROR 700 -PLC. CONVERTOR COMM.FAIL. ON CHECKING THE ERROR, FOUND THAT CCU WAS IN ERROR MODE, THE ERROR CODE IS H1 AND CCU NOT CONNECTED TO LAPTOP, SO WE RESET THE CCU BY PRESSING OF RESET BUTTON IN CCU AND THEN RE-PROGRAM THE CCU FOUND OK THEN RESET THE WTG, DURING THAT TIME AGAIN CCU GOES TO ERROR MODE. HENCE FORTH WE CONFIRMED CCU WAS FAILURE. SO REPLACED THE CCU BY NEW ONE. THEN UPLOAD THE FIRMWARE AND CHECKED ERROR FREE FOUND OK. THERE AFTER WTG PUT BACK INTO OPERATION MO-Field Engineer-Yathavaraj V | SF.NO:- 343 VESM 1 WTG DFM CCU FAILURE-Field Operations Manager-Dhanabal S | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Shankar Anand R.
CIR-10000453	100260065	Sudhan Spinning Mills (P) Ltd	ELAVANTHI	WF-IN-022-0833-Y2-A-007	0.85	65	Standard	Indar	20305001100	Gamesa(China)	601889	High Temperature	STD+	Standard	29/03/2010	402327297	09/04/2016	-0	Yathavaraj V	1370	1437	09/04/2016 00:00:00	09/04/2016 22:00:00	8953990	45970	ELECTRICAL	ELECTRICAL CABINET SYSTEM	50971	QUINT	NORMAL OPERATION	nil	WTG STOPPED DUE TO ERROR 2118.BUS ERROR INTER BUS FAILURE. WE CHECKED THE BUS FAILURE LOG, FOUND THAT THE ERROR CODE 3.0. SO WE CHECKED THE TOP PANEL TIMER CIRCUIT AND POWER SUPPLY UNIT, FOUND TA011 2.5AMPS POWER SUPPLY UNIT FAILED IN CONDITION. SO REPLACED THE FAILURE POWER SUPPLY BY NEW ONE. THERE AFTER WTG PUT BACK INTO OPERATION MODE.	2.5 AMPS POWER SUPPLY UNIT FAILED	DURING NORMAL OPERATION	TOP CONTROL PANEL	POWER SUPPLY WEAK	2.5 AMPS POWER SUPPLY UNIT	VOLTAGE FLUXUATION	01 NUMBER	DURING WTG NORMAL RUNNING TIME TOP PANEL 2.5AMPS POWER SUPPLY UNIT FAILED IN CONDITION.	Assigned	WTG STOPPED DUE TO ERROR 2118.BUS ERROR INTER BUS FAILURE. WE CHECKED THE BUS FAILURE LOG, FOUND THAT THE ERROR CODE 3.0. SO WE CHECKED THE TOP PANEL TIMER CIRCUIT AND POWER SUPPLY UNIT, FOUND TA011 2.5AMPS POWER SUPPLY UNIT FAILED IN CONDITION. SO REPLACED THE FAILURE POWER SUPPLY BY NEW ONE. THERE	WTG STOPPED DUE TO ERROR 2118.BUS ERROR INTER BUS FAILURE. WE CHECKED THE BUS FAILURE LOG, FOUND THAT THE ERROR CODE 3.0. SO WE CHECKED THE TOP PANEL TIMER CIRCUIT AND POWER SUPPLY UNIT, FOUND TA011 2.5AMPS POWER SUPPLY UNIT FAILED IN CONDITION. SO REPLACED THE FAILURE POWER SUPPLY BY NEW ONE. THERE AFTER WTG PUT BACK INTO OPERATION MODE.-Field Engineer-Yathavaraj V | SF.NO:- 686 WTG 230V/2.5AMPS POWER SUPPLY FAILURE-Field Operations Manager-Dhanabal S | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Shankar Anand R.
CIR-10000327	100261646	TANOT WIND POWER VENTURES	Tanot I	WF-IN-020-1490-Y0-A-002	2	90.3	LM	Cantarey	479444	Hansen	EH806A-031/CM0256	High Temperature	STD+	Standard	09/06/2015	402130475	03/10/2015	-0	R.Mariraj	1412	1425	04/10/2015 10:46:00	03/10/2015 20:40:00	1482842	2078	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP091205,GP040684,GP040686		GRID FAILURE		After grid resumed the wtg got error Bus preload protection thermal relay failure.	active crowbar circuit	after grid resumed	converter panel	grid fluctuation	service dept	avoid grid fluctuation	crowbar card-1 IGBT-6 diode-2	WTG got pole test problem and converter circuit got error	Assigned	After grid resumed wtg due to communication error | we checked the DP yard B phase fuse blown | we replaced the fuse and charged the wtg | wtg stop due to error 5212-Bus preload protection thermal relay failure | we checked the WTG found the Active crowbar circuit IGBT , Diode & Driver card was failure | we replaced the smartcrowbar card,IGBT and Diodes	nill-Field Engineer-R.Mariraj | ok-Field Operations Manager-Rajesh Salvi | Power Quality Analysis will be done by Selvamani-Phone Technical Support-Senthil M. | PQA Study recommendation for this WF-Functionality Support Lead-Murugesan P. | -Functionality Support Specialist-Selvamani K.	IMG_20151004_245600219 (1).jpg active crowbar circuit | IMG_20151004_243556669.jpg active crowbar circuit
CIR-10000570	100260656	Lanka transformer ltd	LTL-Srilanka	WF-LK-001-1034-Y0-A-011	0.85	65	Standard	ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	High	12/08/2012	501052661	23/03/2016	-0	P.A.P.Sampath Perera	1386	1439	23/03/2016 17:46:00	23/03/2016 10:10:00	6689092	29781.2	ELECTRICAL	GENERATOR SYSTEM	WP580A,580B,580C,590A,590B	PRYSNIAN CABLE	NORMAL OPERATION	NA	During normal inspection we found that all the power cable outer sheath have damaged (Nacelle frame area & near the HSS down section) & some stretches was observed in under the gearbox power cable holding area. Please find the attached pictures.								May be supplier quality issues.	Assigned	Still not taken any corrective actions. Waiting for STO advice.	Power cable outer sheath crack observations in PD09 turbine at srilanka-Field Engineer-P.A.P.Sampath Perera | Power cable outer sheath crack observed. Pl kindly give your guidance to solve the issues.-Field Operations Manager-Arivazhagan P. | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.	IMG_0026.JPG pl find the cable cracks identification at HSS areas | IMG_1991.JPG power cable stretches observed under the gbx at cable holding areas. | IMG_1992.JPG cable holding area
CIR-10000287	100261005	Lanka transformer ltd	LTL-Srilanka	WF-LK-004-1241-Y0-A-001	0.85	65	Standard	ABB type C	4623693	Rexroth	737000001795	High Temperature	STD+	High	01/06/2013	11	11/04/2016	2118-Interbus bus error	Arivazhagan P.	1381	0	04/04/2016 14:11:00	13/04/2016 14:11:00	121	11	CONTROL SYSTEM	HUB SYSTEM	1	11	GRID FAILURE	11	BIIII
CIR-10000552	100261680	TANOT WIND POWER VENTURES	Tanot I	WF-IN-020-1490-Y0-A-030	2	90.3	LM	Cantarey	801251566	Hansen	EH806A-031/CM0295	High Temperature	STD+	Standard	09/06/2015		27/05/2016	-0	Sunil Jangir	1459	1451	28/05/2016 03:17:00	27/05/2016 12:05:00	2645295	5858	MECHANICAL	HIGH SPEED SHAFT COUPLING SYSTEM		KTR	NORMAL OPERATION														tnt-30 -1.jpg
CIR-10000488	100261626	CLEAN WIND POWER (DEVGARH) PVT.LTD.	GUNGA-G9X	WF-IN-020-1314-Y1-A-004	2	90.3	Infusion (i) - Gamesa	ABB type C	4638299	Hansen	EH806A-031/CM0230	High Temperature	STD+	Standard	03/03/2015	402371398	20/05/2016	-0	Satish Kumar Maurya	1459	1451	21/05/2016 09:05:00	20/05/2016 19:43:00	4953671	10208	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP091181, GP091144, GP040689, GP119052, GP091014	Gamesa	NORMAL OPERATION		Checked and Found IGBT+Adaptor card and simple driver card burnt of phase T.	IGBT+Adaptor card burnt	20.05.2016- 19:43 (During operation)	G97-13 (GS01)	Very high temperature and dust	Service team	Dust protect.	1. Rectifier driver card, 2. Adopter+IGBT 3. Contactor 40A, 690V. 4. Semiconductor Fuse 125A. 5. Resistor 1K & 33 Ohms.		Assigned	Visually Inspect the circuit and found IGBT blast of Rectifier phase T and Resistors in Ingeteam panel. | Replaced the IGBT module/Adopter card with Rectifier driver card and Resistors which was blown out. | Traced the circuit and found semiconductor fuse of 125 Amps blown out. | Further checked and found contactor near Crowbar circuit faulty. | Replaced the Semiconductor fuse. | Replaced the Contactor with auxiliary. | Take a trial which was successful.	Now machine is in normal operation-Field Engineer-Satish Kumar Maurya | closed-Field Operations Manager-Rajesh Salvi | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.	IMG_20160520_225011.jpg IGBT+Adaptor card
CIR-10000341	100261656	CLEAN WIND POWER (DEVGARH) PVT.LTD.	GUNGA-G9X	WF-IN-020-1314-Y1-A-017	2	90.3	LM	ABB type C	4638315	Hansen	EH806A-031/CM0262	High Temperature	STD+	Standard	03/03/2015		30/04/2016	-0	Rajesh Salvi	1422	1425	02/05/2016 22:10:00	30/04/2016 21:45:00	4762700	9690	ELECTRICAL	HUB SYSTEM			NORMAL OPERATION		PWR module internal short , and power supply(TA031) automatically off. FM230 trip ,	FM 230 trigger & hub emergency trigger	30/4/2016 ,21.45	locatio G19 hub	error occured durring running	Satish	reported in action	4 times	PWR module internal sort.	Assigned	Connection(Input/Output) of power supply 3A,5A,10A,20A in hub. | Connection of Power module. | Connection of 230V AC circuit in hub. | Connection of All solenoid coil with cable. | Checked voltage(24V DC) of all module respect to earth. | Replaced PWR module(4 NOS.) | Replaced module (CAB, SEG, AI, DO ,PT )etc. | Connected slip ring joint spares cable from nacelle to hub. | Checked Hub leak sensor. | Checked All 3 blade pressure switch & cable | Inspected hub and found ok, no any leakage in turbine | Hub emergency relay(KR920) replaced	Now turbine run,but under observation-Field Engineer-Charan Singh Bisu | Site Engineer needs more techinical trainings , Spare avaliablity-Field Operations Manager-Rajesh Salvi | confirmation need from Field-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.
CIR-10000401	100261656	CLEAN WIND POWER (DEVGARH) PVT.LTD.	GUNGA-G9X	WF-IN-020-1314-Y1-A-017	2	90.3	LM	ABB type C	4638315	Hansen	EH806A-031/CM0262	High Temperature	STD+	Standard	03/03/2015	402355063	30/04/2016	-0	Satish Kumar Maurya	0	0	02/05/2016 22:25:00	30/04/2016 21:45:00	4762700	9690	ELECTRICAL	HUB SYSTEM	GP009770	Phoenix	NORMAL OPERATION		Relay KR920 and Power Module in Hub Cabinet failure.	Relay KR920 failure	During normal operation	In Hub Panel	Material defect.		Observe it carefully with tracing the circuit.	All related electrical circuit.	Now reset the turbine from display and take an observation. During this observation, we found that when KR920 relay reseted, again pwr module failed. so replaced the Relay & take a trial. Now the trial has successful.	Assigned	Step-01- Checked the circuit and found FM230 tripped. Step-02- Traced the incoming and outgoing circuit of FM230 and found no anyabnormality in the circuit. Step-03- Then switched on the MCB FM230 and FM015 & Observed that there was slightly smoke coming from the power module in Hub Panel. Step-04- Checked the Power Module with all nearby modules and found that the power module was internally short circuited (+Ve & -Ve terminals). So replaced the Power Module. Step-05- Now Removed all mo	We should try to trace the circuit for any abnormalities because there is no any error created without any discrepancy.-Field Engineer-Satish Kumar Maurya | fault finding tree required-Field Operations Manager-Rajesh Salvi | resolved-Phone Technical Support-Senthil M. | -Functionality Support Lead-Shankar Anand R.
CIR-10000281	100261646	TANOT WIND POWER VENTURES	Tanot I	WF-IN-020-1490-Y0-A-002	2	90.3	LM	Cantarey	479444	Hansen	EH806A-031/CM0256	High Temperature	STD+	Standard	09/06/2015	402122299	20/09/2015	-0	R.Mariraj	1383	0	21/09/2015 13:24:00	20/10/2015 16:06:00	0	0	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP091145,GP091181		GRID FAILURE											Deleted
CIR-10000291	100261646	TANOT WIND POWER VENTURES	Tanot I	WF-IN-020-1490-Y0-A-002	2	90.3	LM	Cantarey	479444	Hansen	EH806A-031/CM0256	High Temperature	STD+	Standard	09/06/2015	402130475	03/10/2015	-0	R.Mariraj	1422	1425	04/10/2015 10:46:00	03/10/2015 20:40:00	1482842	2078	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP091205,GP040684,GP040686		GRID FAILURE										WTG pole test not taken	Rejected	After grid resumed wtg due to communication error | we checked the DP yard B phase fuse blown | we replaced the fuse and charged the wtg | wtg stop due to error 5212-Bus preload protection thermal relay failure | we checked the WTG found the Active crowbar circuit IGBT , Diode & Driver card was failure | we replaced the smartcrowbar card,IGBT and Diodes	nill-Field Engineer-R.Mariraj | detail required-Field Operations Manager-Rajesh Salvi | -Field Engineer-Arvind Singh	IMG_20151004_245600219.jpg active crowbar circuit | IMG_20151004_243556669.jpg Active crowbar circuit
CIR-10000767	100261671	TANOT WIND POWER VENTURES	Tanot I	WF-IN-020-1490-Y0-A-019	2	90.3	LM	ABB type C	4638329	Hansen	EH806A-031/CM0291	High Temperature	STD+	Standard	09/06/2015		24/06/2016	-0	Ganesh Ashok Mahajan	0	0	24/06/2016 09:00:00	24/06/2016 05:20:00	0	0	ELECTRICAL	GENERATOR SYSTEM	GP333644	Superior Electic Machines Pvt Ltd	NORMAL OPERATION	69477	While troubleshooting we found generator slipring cooling fan winding failure.	Slipring cooling fan winding failure	On 24.06.2016	In Loc T31	This may be due to excess heat	Mr. M Arvindhan			Fan failure may be lead to high temperature of slipring .	Assigned	We have replaced the cooling fan.	Fan replacement done.-Field Engineer-Ganesh Ashok Mahajan | Fan replaced but identify during other fault finding-Field Operations Manager-Rajesh Salvi | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.	20160625_123816.jpg Old Failure Fan | 20160625_123807.jpg Old Fan Serial Number Plate | CFR No 118 T31 Slipring Cooling Fan Failure.docx
CIR-10000764	100261678	TANOT WIND POWER VENTURES	Tanot I	WF-IN-020-1490-Y0-A-003	2	90.3	Infusion (i) - Gamesa	Cantarey	479450	Hansen	EH806A-031/CM0292	High Temperature	STD+	Standard	09/06/2015		26/06/2016	-0	Ganesh Ashok Mahajan	0	0	01/01/1900 00:00:00	01/01/1900 00:00:00	0	0	MECHANICAL	HIGH SPEED SHAFT COUPLING SYSTEM	GP049319	KTR	NORMAL OPERATION	966	409 Generator-Rotor Discrepancy error occured while big strom We have checked & found coupling torque arm got slipped	Coupling torque arm got slipped	Yesterday	At Location T09		My Self					We have replaced the Coupling		20160626_114645.jpg Old coupling Serial number & torque arm marking mismatched | 20160626_111046.jpg New Coupling Serial Number & Torque arm Marking Matched | 20160626_111108.jpg New Coupling In Operation | CFR No 117 T09 KTR Coupling Replacement.docx
CIR-10000765	100261678	TANOT WIND POWER VENTURES	Tanot I	WF-IN-020-1490-Y0-A-003	2	90.3	Infusion (i) - Gamesa	Cantarey	479450	Hansen	EH806A-031/CM0292	High Temperature	STD+	Standard	09/06/2015		26/06/2016	-0	Ganesh Ashok Mahajan	0	0	01/01/1900 00:00:00	01/01/1900 00:00:00	0	0	MECHANICAL	HIGH SPEED SHAFT COUPLING SYSTEM	GP049319	KTR	NORMAL OPERATION	966	409 Generator-Rotor Discrepancy error occured while big strom We have checked & found coupling torque arm got slipped	Coupling torque arm got slipped	Yesterday	At Location T09		My Self				Assigned	We have replaced the coupling	We have replaced the coupling with a new coupling-Field Engineer-Ganesh Ashok Mahajan | 4th coupling failure at site need RCA-Field Operations Manager-Rajesh Salvi | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Hemkumar D
CIR-10000285	100261638	TANOT WIND POWER VENTURES	Tanot I	WF-IN-020-1490-Y0-A-013	2	90.3		Cantarey	479452	Hansen	EH806A-031/CM0246	High Temperature	STD+	Standard	09/06/2015		10/04/2016	205-Low oil level in hydraulic unit	Ganesh Ashok Mahajan	0	0	10/04/2016 10:50:00	10/04/2016 09:08:00	115898	172	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL			NORMAL OPERATION
CIR-10000396	100261679	TANOT WIND POWER VENTURES	Tanot I	WF-IN-020-1490-Y0-A-014	2	90.3		Cantarey	801251571	Hansen	EH806A-031/CM0293	High Temperature	STD+	Standard	09/06/2015			-0	Ganesh Ashok Mahajan	0	0	01/01/1900 00:00:00	01/01/1900 00:00:00	0	0	MECHANICAL	GEARBOX SYSTEM			NORMAL OPERATION		While blade repair work we found oil leakage from the Gearbox manifold, it may possible that O ring damaged condition.	Found Oil leakage from Gearbox Manifold.	While doing the blade work we found	Near to online filters	It may possible that rubber O ring got damaged	Mr. Ganesh Mahajan			It may possible that rubber o ring got damaged, due to which oil is getting drained & it may lead to failure of Gearbox when oil get full dry.		We have done the visual inspection for oil leakage & found leakage from the manifold & gearbox joint.
CIR-10000305	100261676	TANOT WIND POWER VENTURES	Tanot I	WF-IN-020-1490-Y0-A-018	2	90.3		Cantarey	801251565	Hansen	EH806A-031/CM0290	High Temperature	STD+	Standard	09/06/2015	402253295	22/01/2016	-0	Ganesh Ashok Mahajan	0	0	22/01/2016 17:33:00	22/01/2016 16:33:00	1227589	2564	MECHANICAL	BLADES		LM	NORMAL OPERATION	1542	C blade trailing edge minor damaged while erection of WTG.	Trailing edge damaged	While erection	40M from the Root	may be due to improper handlings	Project		Minor			Ground inspection done, reports shared with concerned persons. | Repair schedule initiated by HO
CIR-10000593	100261141	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-036	0.85	65	Standard	ABB type C	4630534	Hansen	EH806A-001/CM0018	High Temperature	STD+	Standard	29/04/2014	402374934	26/05/2016	-0	Selvan S.	1404	1439	26/05/2016 13:57:00	26/05/2016 11:03:00	3309826	17453	MECHANICAL	GEARBOX SYSTEM	GP057123	Motive	NORMAL OPERATION		WTG stopped due to Gear box fan thermal. Error no:412	Gear box fan thermal.	Running time	Loc No:SVG34	continuous operation	R.Aravindh R.Muthukumar	changed the new one nacelle fan motor	1-No	Material problem,Loose connection ,Continuous operation	Applied	Wtg due to stop We checked digital input, we are attend the found motor connection checking time we found motor U and V winding open condition. | so we replaced new one motor	After replaced motor m/c running normal operation-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	20160607_083717.jpg Nacelle fan motor
CIR-10000282	100261644	TANOT WIND POWER VENTURES	Tanot I	WF-IN-020-1490-Y0-A-010	2	90.3	LM	Cantarey	479466	Hansen	EH806A-031/CM0250	High Temperature	STD+	Standard	09/06/2015	402181150	04/10/2015	-0	R.Mariraj	1422	1425	02/11/2015 23:02:00	02/11/2015 18:40:00	811082	1811	ELECTRICAL	ELECTRICAL CABINET SYSTEM	P393298	ABB	GRID FAILURE		FG001 MPCB was failure during resumed the grid. wtg due to grid voltage failure error occurred	MBCB(0.16A)	Normal operation			service dept			Absence of CCU measuring voltage	Assigned	After grid resume machine was stopped due to grid voltage failure. | we inspected DO fuse found ok | We Inspected transformer 2000A fuse and found ok | While we inspect the voltage at CCU, found voltage got absence. | During inspection found MPCB malfunction. | After replacement of MPCB, Machine in normal operation	NILL-Field Engineer-R.Mariraj | WTG restored-Field Operations Manager-Rajesh Salvi | solved-Phone Technical Support-Senthil M. | resolved-Functionality Support Lead-Murugesan P. | -Quality-Vijay Chinnaswamy	IMG_20151103_113241371.jpg | IMG_20151103_113241371.jpg MPCB(0.16A)
CIR-10000125	100261634	TANOT WIND POWER VENTURES	Tanot I	WF-IN-020-1490-Y0-A-029	2	90.3	Infusion (i) - Gamesa	Cantarey	479432	Hansen	EH806A-031/CM0241	High Temperature	STD+	Standard	09/06/2015		10/03/2016	-0	Rajesh Salvi	1422	1425	10/03/2016 07:56:00	10/03/2016 01:18:00	0	4608	ELECTRICAL	GENERATOR SYSTEM		Lafert	NORMAL OPERATION		WTG manually stopped for Generator fan thermal relay, we observed generator cooling system MPCB tripped.	Motor	10/03/2016 (01:18) Running time.	TNT-19	Winding short with ground	Mariraj R.	By multimeter	1	Winding Temp. will increase.	Assigned	1.Checked MPCB was found healthy | 2.Checked all cable connections of MPCB were found healthy. | 3.Generator external fan operation for low speed & high speed was checked | 4.Check of contactor of generator external fan was carried out which was found healthy. | 5.Checked all relay output, which was found healthy | 6.Checked motor terminal found W phase short with respect to ground | 7.We replaced Generator External Cooling motor with a new one | 8.Checked for normalcies and started the WTG	Due to internal winding short with ground on event of possible insulation failure. -Field Engineer-Victor bhattacharya | Failed-Field Operations Manager-Rajesh Salvi | solved-Phone Technical Support-Senthil M. | Turbine data incomplete (WTG Type )-Functionality Support Lead-Murugesan P. | -Quality-Vijay Chinnaswamy	CFR no 105 Manual stop (generator fan thermal relay) inT-19.pdf CFR | TNT 19.png Motor
CIR-10000293	100261634	TANOT WIND POWER VENTURES	Tanot I	WF-IN-020-1490-Y0-A-029	2	90.3	Infusion (i) - Gamesa	Cantarey	479432	Hansen	EH806A-031/CM0241	High Temperature	STD+	Standard	09/06/2015	402338809	06/04/2016	-0	M.Aravindhan	0	0	06/04/2016 21:14:00	06/04/2016 09:22:00	0	0	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP139206		NORMAL OPERATION		Grid inductor Temperature high	Grid inductor	Normal operation	Nacelle converter side	Resistance value low	Service dept	avoid the grid fluctuation,over voltage and over current	grid inductor-1	Grid inductor Resistance Value Low.	Assigned	Check PT100 sensor & Multiflexer card. | Check the panel cooling fan | Then Clean the panel filter | Check the Resistance value in grid inductor | After we change the Grid inductor	Nill-Field Engineer-M.Aravindhan | turbine restored as Grid inductor failure rate is high in Rajasthan we need analysis-Field Operations Manager-Rajesh Salvi | 8D to be opened for Detailed RCA-Phone Technical Support-Senthil M. | 8D process is recommended-Functionality Support Lead-Murugesan P. | -Quality-Vijay Chinnaswamy	IMG_20151004_243556669.jpg | 2016-04-29 16_34_02-CFR no 801 Excess temp of grid inductor T-19.jpg | 2016-04-29 16_34_27-CFR no 801 Excess te2mp of grid inductor T-19.jpg | CFR no 801 Excess temp of grid inductor T-19.pdf
CIR-10000509	100261620	CLEAN WIND POWER (DEVGARH) PVT.LTD.	GUNGA-G9X	WF-IN-020-1314-Y1-A-010	2	90.3	LM	ABB type C	4638294	Hansen	EH806A-031/CM0122	High Temperature	STD+	Standard	03/03/2015		28/05/2016	-0	Satish Kumar Maurya	1459	1451	28/05/2016 07:42:00	28/05/2016 03:40:00	5156678	10316	CONTROL SYSTEM	HUB SYSTEM			NORMAL OPERATION		Hub hydraulic leak, 5201-Magnetothermic trigger of the stator protection	Hub light got damaged.	During normal operation	In hub area	Tube light mounting base is of plastic/weak materials.	Service team	Base of tube light assembly should be of metallic body.	Hub light assembly only.	One by one another fault came that's why the breakdown duration increased.	Assigned	Checked and reset the Air Circuit Breaker. | Sound observed in hub so went into hub and found hub light assembly badly damaged. | Removed all damaged part of hub light and mounting plate. | Visually inspection done for any damages in the hub and found all other cables, sensors and pipes were in ok condition. | Now take a trial but after generation start, the error 212-Hub hydraulic leak. | Removed the hub leak sensor and checked its connection and found Cable shield wire was in open condition. | So connect it and properly tight and then take a trial and it was successful.	Hub light assembly base should be of metallic body.-Field Engineer-Satish Kumar Maurya | turbine running-Field Operations Manager-Rajesh Salvi | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Anand A.P
CIR-10000675	100261665	TANOT WIND POWER VENTURES	Tanot I	WF-IN-020-1490-Y0-A-012	2	90.3	Infusion (i) - Gamesa	ABB type C	4638319	Hansen	EH806A-031/CM0277	High Temperature	STD+	Standard	09/06/2015		10/06/2016	-0	Ganesh Ashok Mahajan	0	0	01/01/1900 00:00:00	01/01/1900 00:00:00	3482114	0	MECHANICAL	BLADE BEARING SYSTEM			NORMAL OPERATION		We went to WTG for Smoke sensor replacement at that time we heard some sound from Hub, so we have checked & found A blade bearing inner rubber seal was completely removed while normal operation.	A blade bearing inner seal removed	On 10.06.2016 we have seen	In Hub	It may possible that seal joint first open then full seal while normal operation	Mr. Saurabh Pachori			1. If this seal removed the dust will go inside & it may possible that bearing balls may got damage. 2. If we run the WTG it may possible that grease may came out. 3.	Assigned	We have taken the seal & started the WTG.	Seal Removed, have to replace as earlier as possible.-Field Engineer-Ganesh Ashok Mahajan | expert help & material required for restoration-Field Operations Manager-Rajesh Salvi | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Anand A.P	20160612_104853.jpg Seal Removed | 20160612_104910.jpg Seal Removed from Blade A | 20160612_104503.jpg B Blade Seal is in good condition | 20160612_104829.jpg C Blade Seal is in good condition | 20160610_121827.jpg Seal removed & is in this condition while WTG running
CIR-10000284	100261638	TANOT WIND POWER VENTURES	Tanot I	WF-IN-020-1490-Y0-A-013	2	90.3		Cantarey	479452	Hansen	EH806A-031/CM0246	High Temperature	STD+	Standard	09/06/2015		10/04/2016	-0	Ganesh Ashok Mahajan	0	0	10/04/2016 10:50:00	10/04/2016 09:08:00	115898	172	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL			NORMAL OPERATION		A hydraulic hose who is coming to hub from nacelle is got damaged while rubbing with return oil tank.	Main oil hose who coming from nacelle to hub got slightly damaged.	On 10.04.2016	Near to Return oil tank in HUB	Due to rubbing with return oil tank	Nacelle to Hub Hose		Slightly, but leakage started		Assigned	Since it was slightly leakage, so we have not done nothing but WTG is under observation.	We have to replace the hose as soon as possible, preferably before High wind-Field Engineer-Ganesh Ashok Mahajan | need protection for hose pipe-Field Operations Manager-Rajesh Salvi | 8D must open for detailed failure control action plan-Phone Technical Support-Senthil M. | Containment Action - Proper routing of Hydraulic hoses, WTG under observation, Vijay - Please check the RCA for this issue-Functionality Support Lead-Anand A.P | provide a suitable a time to discuss this issue in , we may need site for this meeting-Quality-Vijay Chinnaswamy | As discuused with Mahagan, one one case observed. The hose to be replaced and the cover beeding to be fixed to protect the hose damage. Issue closed-Functionality Support Lead-Anand A.P | -Quality-Vijay Chinnaswamy	20160410_101141.jpg | 20160410_101141.jpg Hose rubbing with Return Oil tank | 20160410_101511.jpg Hose Damaged Portion
CIR-10000169	100260575	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-106-MDN	0.85	65	Standard	Gamesa wind Tianjin, China	801001200	Gamesa(China)	602550	High Temperature	STD+	Standard	31/12/2014	402261241	08/02/2016	3247-Disconnection timeout	Selvan S.	1404	1425	08/02/2016 16:00:00	08/02/2016 10:50:00	1495492	9396	ELECTRICAL	GENERATOR SYSTEM	P390157	Baumer Hubner	NORMAL OPERATION	2279885	error No 3247 Disconnection timeout	Disconnection timeout	running time	running time	manufacture defect	Encoder	Rpm measuring wrong	1 encoder	Manufacture Defect	Assigned	Wtg stopped | Check the alarm log | We checked digital input | We checked GENERATOR ENCODER | Encoder input signal not coming | ENCODER found not working properly | We found GENERATOR ENCODER Failure confirmed | replaced the new one ENCODER	Manufacture defect-Field Engineer-Selvan S. | Approved-Field Operations Manager-Sivakumar S. | closed-Phone Technical Support-Senthil M. | This is also Top 20 component failure list . We will take it as project-Functionality Support Lead-Murugesan P. | -Quality-Vijay Chinnaswamy	IMG_20160308_161206.jpg
CIR-10000342	100260877	National Aluminium Company Limited	JAISALMER	WF-IN-020-1070-Y0-A-040	0.85	65	Standard	ABB type C	4622191	Gamesa gearbox	100847	High Temperature	HD	Standard	26/05/2013		30/04/2016	-0	Ravi Kumar Verma	1404	1460	01/05/2016 01:40:00	30/04/2016 19:40:00	3092517	24507.92	ELECTRICAL	TRANSFORMER SYSTEM		Gawde	NORMAL OPERATION	4607/18	DURING NORMAL OPERATION COMBINE METERING CTPT GET FAIL AND FEEDER TRIPPED. OIL GET LEAKAGE FROM CTPT.	CTPT GET FAIL AND FEEDER TRIPPED. OIL GET LEAKAGE FROM CTPT.	NORMAL OPERATION	AT HT YARD METRING POINT		RAVI VARMA		THIS SECOND TURBINE IN WHICH CTPT FAIL.	DURING NORMAL OPERATION COMBINE METERING CTPT GET FAIL AND FEEDER TRIPPED. OIL GET LEAKAGE FROM CTPT. THIS IS SECOND CTPT FAIL IN SAME FEEDER.	Assigned	1. CHECK TRANSFORMER MAGGER VALUE. | 2. CHECK FUSE AND FOUND OK. | 3. CTPT CONNECTION REMOVE AND TRANSFORMER CHARGE.	TWO TURBINE CTPT GET FAIL NEED INSPECTION CHECK LIST FOR OTHER TURBINE .-Field Engineer-Ravi Kumar Verma | 2 nd CTPT failure ( Meter reading pending due to failure)-Field Operations Manager-Rajesh Salvi | BOP Inspection recommended-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.
CIR-10000338	100260852	National Aluminium Company Limited	JAISALMER	WF-IN-020-1070-Y0-A-042	0.85	65	Standard	ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	HD	Standard	26/05/2013	402327655	01/04/2016	-0	Bhanwar Singh Chouhan	1394	1460	01/04/2016 23:10:00	01/04/2016 17:40:00	2970940	23719.23	ELECTRICAL	TRANSFORMER SYSTEM		GAWDA	GRID FAILURE										Metering CTPT unit Y-phase found failed during grid fluctuation.	Assigned	1. CHECK TRANSFORMER IR VALVU | 2. FOUND OK | 3. 1000A FUSE CHECK AND REPLACED BY NEW ONE. | 4. CTPT CONNECTION REMOVE. | 5. CHARGE THE TRANSFORMER.	SUGGEST FOR OTHER LOC CHECK POINT.-Field Engineer-Bhanwar Singh Chouhan | 2 CTPT failure at site need material to meter reading (Ramesh sir)-Field Operations Manager-Rajesh Salvi | Detailed investigation will be done by Selvamani-Phone Technical Support-Senthil M. | Please any inspection is recommended or not-Functionality Support Lead-Murugesan P. | -Functionality Support Specialist-Selvamani K.	DSC09639.JPG | DSC09650.JPG
CIR-10000389	100260940	National Aluminium Company Limited	JAISALMER	WF-IN-020-1070-Y0-A-063	0.85	65	Standard	ABB type C	4622191	Gamesa gearbox	100847	High Temperature	HD	Standard	22/06/2013		08/05/2016	-0	Dwarkaram Panwar	1414	1439	01/01/1900 00:00:00	08/05/2016 14:48:00	3287923	23440.21	ELECTRICAL	NACELLE INSTRUMENTATION SYSTEM			GRID FAILURE		High Voltage occur from Amarsagar( Govt. Pooling Station), and our substation (Ludarwa) also tripped in High voltage. After 30 min grid restore, many turbine was in error so our team was attending the turbine one by one. When we reached at NGL08( NALCO Turbine) it was showing error 3.0 in PLC. One of the Operator Mr.Sher Singh clime in Nacelle to attend the error, he saw there was fire in cable near gear Box. He immediate use the Fire extinguisher and Dwarka Ram to isolate the Turbine. Top to bottom,Gearbox sensor and Hyd system cable burn.	sensor and control cable	during grid fail	Nacelle	breaking	sher singh Dwarka ram			gear box Hyd. system and top to bottom cable get damage.	Assigned	use the fire Extinguser and control the fire. | 2. Disconnect the power.	Mr. SIVARAJAN, VENKATESH inspact the wtg.-Field Engineer-Dwarkaram Panwar | STO ,quality and safety team visited site deatailed RCA and materials required for restoration-Field Operations Manager-Rajesh Salvi | Pls assign to Venkadesh for detailed RCA-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.
CIR-10000444	100261116	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-037	0.85	65	Standard	ABB type C	4630534	Hansen	EH806A-001/CM0018	High Temperature	STD+	Standard	29/04/2014	402326262	06/04/2016	805-Pitch Blocked	Selvan S.	1404	1439	06/04/2016 14:41:00	06/04/2016 13:32:00	2921351	16067	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	880162	Vickers	NORMAL OPERATION		Error No :800. Pitch Activation Error.	Error No :800. Pitch Activation Error	Running time	Loc no:SVG35 HU unit	Continuous operation, material defective.	D.Manoj, R.Aravindh, K.Magesh	Change the new one proportional valve.	1-no	Continuous operation, Unbalance load, pitch angle , blade weight.	Applied	we checked the Digital input, normal running time HU pressure decrease checked the Proportional valve Malfunctioning in running time, So we confirmed the proportional valve was failure, replaced new one valve.	Turbine running with normal operation-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	smp.jpg Proportional valve | Proportional valve.JPG Proportional valve
CIR-10000408	100261280	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-094-MDN	0.85	65	Reinforced	ABB type C	4630879	Hansen	EH806A-001/CM0117	High Temperature	STD+	Standard	31/12/2014	402254851	02/02/2016	2118-Interbus bus error	Selvan S.	1404	1439	02/02/2016 18:49:00	02/02/2016 16:49:00	1556682	9164	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004896	PHOENIX	NORMAL OPERATION	7000512415
CIR-10000409	100260575	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-106-MDN	0.85	65	Standard	Gamesa wind Tianjin, China	801001200	Gamesa(China)	602550	High Temperature	STD+	Standard	31/12/2014		08/02/2016	3247-Disconnection timeout	Selvan S.	1404	1439	08/02/2016 16:35:00	08/02/2016 13:00:00	1494227	9353	ELECTRICAL	GENERATOR SYSTEM	GP006135	Gamesa	NORMAL OPERATION		Error No 3247. Disconnection timeout error occurred								voltage dip, may be problem for ccu communication port	Applied	Stop the m/c | Check the digital input | We checked the related connection | While checking we found CCU got failure it was replaced by new one	Wtg due to stop we are attend and found check the CCU got failure condition.so replaced new one then start the WTG.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	dfim.jpg CCU
CIR-10000410	100260575	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-106-MDN	0.85	65	Standard	Gamesa wind Tianjin, China	801001200	Gamesa(China)	602550	High Temperature	STD+	Standard	31/12/2014		08/02/2016	3247-Disconnection timeout	Selvan S.	1404	1439	08/02/2016 16:35:00	08/02/2016 13:00:00	1494227	9353	ELECTRICAL	GENERATOR SYSTEM	GP006135	Gamesa	NORMAL OPERATION
CIR-10000574	100260567	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-112-MDN	0.85	65	Reinforced	Gamesa wind Tianjin, China	447631	Gamesa(China)	602475	High Temperature	STD+	Standard	31/12/2014	402371216	14/05/2016	2118-Interbus bus error	Selvan S.	1404	1439	14/05/2016 19:23:00	14/05/2016 18:10:00	1863191	11614	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004891	PHOENIX	NORMAL OPERATION		Error No 2118: Bus Error / Inter bus Failure	Error No 2118: Bus Error / Inter bus Failure	Running time	Loc no- SVG43: Top panel	Grid fluctuation	D.Manoj R.Aravindh R.Muthukumar	Changed the SEG module	1-No	Frequent operation,Material problem Short circuit, Loose connection	Applied	Wtg due to stop We checked digital input, we are attend the found PLC displayed CTRL code 3.13 We found SEG-ELF module Failure confirmed.New one SEG-ELF module replaced , then start the WTG.	After replaced the Module turbine with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	SEG MODULE.JPG SEG MODULE
CIR-10000402	100261628	CLEAN WIND POWER (DEVGARH) PVT.LTD.	GUNGA-G9X	WF-IN-020-1314-Y1-A-016	2	90.3	LM	ABB type C	4638289	Hansen	EH806A-031/CM0237	High Temperature	STD+	Standard	03/03/2015	402325593	31/03/2016	-0	Satish Kumar Maurya	0	0	03/05/2016 11:17:00	02/04/2016 14:40:00	4319821	9149	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP091144		NORMAL OPERATION		The Error in phase R of the Rectifier. IGBT Driver Card Failure.	Rectifier Driver Card Failure	During normal operation	Ingeteam panel	component failure		Replaced the pcb Rectifier Driver Card.	R phase of the Rectifier.	Replaced the Driver Card of R phase of the Rectifier and the problem has resolved.	Assigned	Visually checked all components in Ingeteam panel and found no any discrepancy in it. Now individual testing done of IGBT and diode and found all were ok.	There should be a specific procedure for testing the Printed Circuit Board (PCB).-Field Engineer-Satish Kumar Maurya | turbine running-Field Operations Manager-Rajesh Salvi | resolved-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.
CIR-10000510	100261628	CLEAN WIND POWER (DEVGARH) PVT.LTD.	GUNGA-G9X	WF-IN-020-1314-Y1-A-016	2	90.3	LM	ABB type C	4638289	Hansen	EH806A-031/CM0237	High Temperature	STD+	Standard	03/03/2015	402355084	05/05/2016	-0	Satish Kumar Maurya	1459	1451	05/05/2016 09:36:00	05/05/2016 05:36:00	5105766	9674	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP132052		NORMAL OPERATION		Error in phase S of the inverter.	Thyrister	Normal running condition (Before 05 hours of this fault, there was grid failure.)	In Inseteam panel	Become weak due to grid failure frequently.	Service team	Checked and replaced the Thyrister.	Prevent the grid failure.	Before it, the error came frequently.	Assigned	Visually checked the Ingeteam panel and Chokes and found all were ok. | Now individually checked the Thyristers, Diodes, and contactor and found Thyrister was faulty. | Replaced the thyrister with new one. | Take a trial and it was successful.	Prevent grid failure frequently.-Field Engineer-Satish Kumar Maurya | Spares replaced ,turbine running-Field Operations Manager-Rajesh Salvi | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.
CIR-10000592	100260571	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-104-MDN	0.85	65	Standard	Gamesa wind Tianjin, China	801001290	Gamesa(China)	602575	High Temperature	STD+	Standard	31/12/2014	501026704	18/05/2016	-0	Selvan S.	1404	1439	18/05/2016 16:24:00	18/05/2016 15:18:00	1655147	11742	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	GP004893	Olaer	NORMAL OPERATION		Wtg Manually stopped for 18month maintenance work, mean time pitch accumulator failure.	Accumulator failure	Maintenance time	Loc No:SVG172	continuous operation	D.Manoj R.Aravindh R.Muthukumar	changed the new one pitch accumulator	1-No	Continuous operation,	Applied	During service time old pitch accumulator remove and refilled the another one accumulator that accumulator fixing thread already damaged condition, so replaced the new one accumulator. | We replaced it by new one Accumulator and restarted the turbine.	After replaced the Pitch accumulator m/c running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	20160607_083400.jpg Pitch Accumulator
CIR-10000433	100260909	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-006	0.85	65	Standard	ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	29/04/2014	501016775	06/04/2016	-0	Selvan S.	1404	1439	06/04/2016 19:09:00	06/04/2016 17:49:00	3327418	16401	MECHANICAL	GEARBOX SYSTEM	GP057123	FLUITECNIK	NORMAL OPERATION		During maintenance time error no:412 Gearbox fan thermals error occurred.	Gear box fan thermal. Error no:412	During maintenance time	Nacelle cooling fan motor.	Weak the motor coils	R.Muthukumar M.Muthu A.Sathish	New one Nacelle cooling motor replaced.	1-No	During long time operation so weak the motor coils, loose connection.	Applied	Wtg stopped for error no:412 occurred. | Check the digital input. | Cooling fan motor one phase short circuit. | Remove the old nacelle cooling fan motor. | Replaced the new one Nacelle cooling motor. | All related connection checked. | Nacelle cooling fan Testing run checked found normal operation.	After replaced the Naccele Cooling motor turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	HTDC FAN.jpg HTDC Fan Motor
CIR-10000596	100261133	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-020	0.85	65	Standard	ABB type C	4630534	Hansen	EH806A-001/CM0018	High Temperature	STD+	Standard	29/04/2014	402386562	02/06/2016	113-Yaw motors thermomagnetic relay failure	Selvan S.	1404	1439	02/06/2016 22:21:00	02/06/2016 16:59:00	3083917	17600	MECHANICAL	YAW SYSTEM	GP056119	ABB	NORMAL OPERATION		Error No :113. Yaw motors thermomagnetic relay failure	Error No :113. Yaw motors thermomagnetic relay failure	Running time	Loc No:SVG52	Over current happened due to the Motor winding insulation failed.	D.Manoj R.Muthukumar	Changed the new one yaw motor	1-No	Material problem,Loose connection ,Grid Fluctuation	Applied	Error No :113. Yaw motors thermomagnetic relay failure error occurred. Checked and found Thermal relay FT181 was tripped. | So we checked the yaw motor circuits and found coupling side Yaw motor winding was short circuit with ground. So we confirmed the motor was failed | Failed motor was replaced with new one.	motor changed after m/c running normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	20160607_083519.jpg YAW motor
CIR-10000435	100261320	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-096	0.85	65	Reinforced	ABB type C	4633323	Hansen	EH806A-001/CM0157	High Temperature	STD+	Standard	10/08/2014	402336025	16/04/2016	2118-Interbus bus error	Selvan S.	1404	1439	16/04/2016 14:58:00	16/04/2016 14:12:00	2104544	14163	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP004896	PHOENIX	NORMAL OPERATION		Error No 2118: Bus Error / Inter-bus Failure.	Error No 2118: Bus Error / Inter-bus Failure	During running time	Loc no:SVG193 top cabinet panel	malfunctioning the module.	D.Manoj, R.Aravindh, R.muthukumar	Changed the new one module.	1- No	Malfunctioning the module and Environmental weather change.	Applied	Stopped the m/c. | Checked the Digital input. | Check the HMI log Alarm and warning list Shows 3.15 | We have checked and found that RS485/422 module was failure | So the RS485/422 module was changed and wtg restarted.	After replaced the RS485/422 module turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	IMG_20160308_161143.jpg Module RS485/422
CIR-10000170	100261321	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-095-MDN	0.85	65	Reinforced	ABB type C	4633323	Hansen	EH806A-001/CM0157	High Temperature	STD+	Standard	31/12/2014	402268525	15/02/2016	-0	Selvan S.	1404	1425	15/02/2016 17:16:00	15/02/2016 15:06:00	3283915	13584	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP004895	Phoenix	NORMAL OPERATION	7000514715	2118. Bus error Inter bus fail error	m/c stopped	Running time	Top panel	surge voltage	D.Manoj R.Aravindh	Plc displayed 3.11	one temp rtd module	Surge voltage.	Assigned	Wtg stopped | check the digital input | PLC displayed CTRL code 3.11 nos | so we confirmed temp module failure | Replaced new one Temp RTD module | Restart the m/c	Surge voltage-Field Engineer-Selvan S. | Aproved-Field Operations Manager-Sivakumar S. | Closed-Phone Technical Support-Senthil M. | Problem solved after the replacement-Functionality Support Lead-Shankar Anand R.	AI MODULE.jpg | IMG_20160308_160905.jpg
CIR-10000579	100261321	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-095-MDN	0.85	65	Reinforced	ABB type C	4633323	Hansen	EH806A-001/CM0157	High Temperature	STD+	Standard	31/12/2014	402371236	23/05/2016	2118-Interbus bus error	Selvan S.	1404	1439	23/05/2016 19:00:00	23/05/2016 18:20:00	1908850	11754	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004891	Phoenix	NORMAL OPERATION		Error No 2118: Bus Error / Inter-bus Failure	Bus Error / Interbus Failure	Running time.	LOC NO:SVG180	Surge voltage, continuous operation	R.Aravindh D.Manoj R.Muthukumar	Change the SEG Module	1-No	Surge voltage, continuous operation	Applied	Wtg due to stop We checked digital input, we are attend the found PLC displayed CTRL code 3.13 We found SEG-ELF module Failure | New one SEG-ELF module replaced , then start the WTG	After replaced the module turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	SEG MODULE.JPG SEG module
CIR-10000355	100260855	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-056	0.85	65	Standard	ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	29/06/2014	402224724	02/01/2016	2112-TOP supply failure	Sivakumar S.	1404	1425	02/01/2016 17:43:00	02/01/2016 14:28:00	2423482	13051	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP144138	Wiedmuller	NORMAL OPERATION	8951360000										Deleted	CIR create in double time
CIR-10000437	100260635	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-110-MDN	0.85	65	Reinforced	ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	31/12/2014	402341617	20/04/2016	113-Yaw motors thermomagnetic relay failure	Selvan S.	1404	1439	21/04/2016 23:00:00	20/04/2016 23:15:00	1598994	10560	ELECTRICAL	YAW SYSTEM	GP019624,GP015709,GP075083	Phoenix, ABB	NORMAL OPERATION		Yaw motors thermo magnetic relay failure.	Yaw motors Thermomagnetic relay failure	running time	Loc no:SVG177 Yaw system	continuous operation.	D.Manoj, R.Aravindh, R.Muthukumar, A.Sathish	Changed the one contactor A26 30 10, Changed the new one 690v MPCB, Changed the New one 24DO 32/HD module.	Each one No	during long time operation, malfunctioning the module.	Applied	Wtg due to stopped | Checked the digital input. | CW motor contactor failure replace the new one A26-30-10 contactor. | Changed the new one MPCB | Changed the 24DO 32/HD module changed. | all related connection checked. | then start the wtg.	Turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	CNT Module.jpg module 24DO 32/HD | 20160519_142118.jpg AL16-30-10 contactor | 20160519_142240.jpg 20-25A MCB
CIR-10000571	100260635	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-110-MDN	0.85	65	Reinforced	ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	31/12/2014	501027207	11/05/2016	111-Max hydraulic unit pumping time	Selvan S.	1404	1439	11/05/2016 19:00:00	11/05/2016 14:43:00	1660189	11016	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	103846, 565590	Gamesa	NORMAL OPERATION		During 18 month service time error:111 Max hydraulic unit pumping time error occurred	Error No 111: Max hydraulic unit pumping time	During 18 month service time	Hydraulic unit	Unbalance load, continuous operation	D.Manoj R.Aravindh R.Muthukumar	New one HU valve block , one needle valve replaced ,	Hydraulic unit valve block -1no Needle valve - 1 No	Unbalance load, continuous operation , Quality of pitch cylinder , no air flowing , over heat, grid failure , pitch angle,	Applied	We checked the digital input | hydraulic pressure is not devoloping , motor continuous on not cut off the HU Unit motor ,we checked the motor found normal operation, Hydraulic unit valve block entire side blocking the oil, found hydraulic valve block failure confirmed. | New one HU valve block , one needle valve replaced , then start the WTG	Turbine running normal condition.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	20160519_163632-1.jpg Hydraulic unit valve block
CIR-10000572	100260635	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-110-MDN	0.85	65	Reinforced	ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	31/12/2014	402363814	11/05/2016	111-Max hydraulic unit pumping time	Selvan S.	1404	1439	13/05/2016 11:52:00	11/05/2016 19:00:00	1660189	11016	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	GP057228, GP004261, 131071	Gamesa	NORMAL OPERATION		Error No 111: Max hydraulic unit pumping time	Max hydraulic unit pumping time	normal running time	HU Unit	continuous operation,no air flowing	R.Aravindh R.Muthukumar S.Selvan D.Manoj	New one Yaw manifold valve block ,relief valve, Relay base each one replaced ,	Yaw manifold valve block -1 no, Relay base-1 No, Relief valve- 1 No	Unbalance load, continuous operation , Quality of pitch cylinder , no air flowing , over heat, grid failure , pitch angle , blade weight	Applied	WTG stopped due to error:111 Max hydraulic unit pumping time error occurred | We checked the digital input, hydraulic pressure is not developing ,Yaw pressure also not developing motor continuous on not cut off the HU Unit motor ,we checked yaw manifold block accumulator pressure is fine, but relief valve pressure is not developing. Yaw block got failure confirmed, also relay base and relief valve got failure confirmed. | New one Yaw manifold valve block ,relief valve, Relay base each one replaced , then start the WTG	After replaced the yaw block valve, relay base, relief valve turbine running with normal operation-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	20160519_163600.jpg Yaw manifold valve block | GP004261.jpg relay base
CIR-10000598	100260635	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-110-MDN	0.85	65	Reinforced	ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	31/12/2014	402371218	19/05/2016	805-Pitch Blocked	Selvan S.	1404	1439	19/05/2016 02:05:00	18/05/2016 23:43:00	1685338	11164	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	GP004898, GP010568	PHOENIX	NORMAL OPERATION		Wtg stopped due to error no:800 Pitch activation occured	error no:800 Pitch activation	Running time	Loc no:SVG177	Continuous Operation,voltage fluctuation	R.Muthukumar R.Aravindh	one AO module and 6A relay replaced.	each one no's	This component was failure due to Continuous Operation,voltage fluctuation and material defect.	Applied	We checked digital input, We checked and found AO module got malfunctioning, relay also failure, found not working properly ,We found AO module and relay failure confirmed, so replaced the new one, then start the WTG	After replaced the AO module and 6A relay turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	PLC RELAY 6A.jpg Relay 6A | DSC_0089.jpg AO module
CIR-10000139	100260575	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-106-MDN	0.85	65	Standard	Gamesa wind Tianjin, China	801001200	Gamesa(China)	602550	High Temperature	STD+	Standard	31/12/2014	402239771	19/01/2016	-0	Selvan S.	1404	1425	19/01/2016 14:27:00	19/01/2016 12:42:00	1646	8926	ELECTRICAL	SOFTWARE	GP006135	Gamesa	NORMAL OPERATION		Bus error Inter-bus fail error occurred								Material Defective	Rejected	Wtg stopped | Check the digital input | PLC displayed CTRL 2.0 | We found CCU failure | new one CCU | Restart the M/C	Supply failure time CCU failed-Field Engineer-Selvan S. | Approved-Field Operations Manager-Sivakumar S. | closed-Phone Technical Support-Senthil M. | Explain in detail about the failure . Error related to Interbus error & then why CCU has been replaced?-Functionality Support Lead-Shankar Anand R. | -Field Engineer-Aravind Kumar J.	dfim.jpg
CIR-10000406	100260899	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-054	0.85	65	Standard	ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	29/04/2014	402303270	11/03/2016	-0	Selvan S.	1404	0	11/03/2016 15:14:00	11/03/2016 14:07:00	2434721	15257	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004898	Gamesa	NORMAL OPERATION		BUS error - INTER-BUS failure	Error No 2118. Bus error Inter-bus fail error occurred.	During running time	SVG68 top panel	Malfunctioning the module	D.Manoj, S.Selvan	Change the new one AO module	1- no	This AO module failure due to malfunctioning, surge voltage.	Applied	Wtg stopped due to Error no:2118 Inter bus Error.When turbine running this error occurred.We see the alarms in HMI log it shows on 3.18. We have checked and found that AO module was failure. So the AO module was changed and wtg restarted.	After replaced the AO module turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	DSC_0089.jpg AO module
CIR-10000578	100261279	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-097	0.85	65	Reinforced	ABB type C	4630879	Hansen	EH806A-001/CM0117	High Temperature	STD+	Standard	11/08/2014	402371235	23/05/2016	2118-Interbus bus error	Selvan S.	1404	1439	23/05/2016 19:40:00	23/05/2016 16:56:00	2115011	14893	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004898	Phoenix	NORMAL OPERATION		Error No 2118: Bus Error / Inter bus Failure	Bus Error / Interbus Failure	Running time	LOC NO:SVG194	continuous operation	D.Manoj R.Aravindh R.Muthukumar	changed the AO module	1-No	Frequent operation,Material problem Short circuit, Loose connection.	Applied	Wtg due to stop We checked digital input, we are attend the found PLC displayed CTRL code 3.18. We found AO module Failure | We found AO module Failure confirmed, so replaced the new one module	Turbine running normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	DSCN1566.JPG AO module | DSC_0089.jpg AO module
CIR-10000594	100261279	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-097	0.85	65	Reinforced	ABB type C	4630879	Hansen	EH806A-001/CM0117	High Temperature	STD+	Standard	11/08/2014	402376764	28/05/2016	3232-Synchronization timeout	Selvan S.	1404	1439	28/05/2016 17:11:00	28/05/2016 12:47:00	2143297	14992	MECHANICAL	GENERATOR SYSTEM	GP038819	Baumer Hubner	NORMAL OPERATION		After voltage fluctuation time error No:3232 Synchronization Timeout	error No:3232 Synchronization Timeout	Running time	Loc no:SVG194	continuous operation	R.Muthukumar R.Aravindh	changed the encoder coupler	1-No		Applied	Wtg due to stop We checked digital input, We checked GENERATOR ENCODER found ok, Coupler got damaged working not properly, We found GENERATOR ENCODER COUPLER Failure confirmed, so replaced the new one Coupler, then start the WTG.	Frequent operation,Material problem-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	IMG_20160308_161230.jpg Encoder coupler
CIR-10000243	100260699	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-012	0.85	74		ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	14/03/2014		28/03/2016	-0	Ram Lakshmanan MP	1386	1425	28/03/2016 15:40:25	28/03/2016 15:30:25	3406112	17293	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL			NORMAL OPERATION		During 24 month service pitch cylinder leak								pitch cylinder leak	Assigned	need suggustion	Need suggustion-Field Engineer-Ram Lakshmanan MP | Need your suggustion-Field Operations Manager-Ravibala Suresh S. | Detailed investigation recommended-Phone Technical Support-Senthil M. | Required detailed investigation-Functionality Support Lead-Anand A.P | -Functionality Support Specialist-Babu M.
CIR-10000135	100261115	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-103	0.85	65	Standard	ABB type C	4630534	Hansen	EH806A-001/CM0018	High Temperature	STD+	Standard	21/08/2014	402224722	02/01/2016	3403-Rotor contactor feedback failure (KM052R)	Selvan S.	1404	1425	02/01/2016 17:26:00	02/01/2016 14:48:00	1698696	11518	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP019639	Semikron, ABB	NORMAL OPERATION	7000507401	Wtg during running time Rotor Conductor Feedback Failure error occurred.	rotor contactor feedback failure	during running time	bottom panel	grid fluctuation	converter panel			Error occurred due to input voltage problem in circuits	Assigned	Wtg stopped | Wtg due to stop We checked digital input | rotor contactor Jammed | We found Rotor skip module and rotor contactor Failure confirmed | replaced the new one module and contactor	Grid fluctution time some component failure-Field Engineer-Selvan S. | Approved-Field Operations Manager-Sivakumar S. | further investigation recommanded-Phone Technical Support-Senthil M. | DAC CCU trigger configuration to be installed-Functionality Support Lead-Murugesan P. | Failed component to inspected for failure mode.-Functionality Support Specialist-Mayank | -Quality-Vijay Chinnaswamy	skip module.jpg | s.jpg | 50 30 contactor.jpg
CIR-10000411	100260504	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-105-MDN	0.85	65	Standard	Gamesa wind Tianjin, China	801001181	Gamesa(Spain)	400889	High Temperature	STD+	Standard	31/12/2014	402276246	18/02/2016	2118-Interbus bus error	Selvan S.	1404	1439	18/02/2016 18:00:00	18/02/2016 06:48:00	1571410	9628	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP006135, GP005798	Gamesa	NORMAL OPERATION		Error No 2118. Bus error Inter-bus fail error occurred								surge voltage fluctuation	Applied	stop the m/c | check the HMI log alarm | So we checked related connection While checking we found CCU got failure it was replaced by new one | One brake thermistor pad replaced	we are attend and found check the ccu got failure and Brake thermistor pad new one replaced, then start the WTG.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	dfim.jpg CCU | IMG_20160108_124109.jpg Brake thermistor pad
CIR-10000665	100260504	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-105-MDN	0.85	65	Standard	Gamesa wind Tianjin, China	801001181	Gamesa(Spain)	400889	High Temperature	STD+	Standard	31/12/2014	402389550	09/06/2016	2118-Interbus bus error	Selvan S.	1404	1439	09/06/2016 23:59:00	09/06/2016 19:21:00	1893806	12246	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004894	Phoenix	NORMAL OPERATION		Error No :2118. BUS error - INTERBUS failure	Error No :2118. BUS error - INTERBUS failure.	Normal operation time	Loc no:SVG94	Grid Fluctuation,Material defective,Input voltage problem	A.Satish, R.Aravindh	Changed the CNT module	1- No	Grid Fluctuation,Material defective,Input voltage problem	Applied	we checked the Digital iput | While inspection we found CNT module LED was red indication occurred then conclude CNT module failure then replaced the new one wtg operation normal	After replaced the CNT module turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	CNT Module.jpg CNT module
CIR-10000423	100261263	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-080	0.85	65	Reinforced	ABB type C	4630879	Hansen	EH806A-001/CM0117	High Temperature	STD+	Standard	04/06/2014	402296915	03/03/2016	2118-Interbus bus error	Selvan S.	1404	1439	03/03/2016 13:22:00	03/03/2016 12:00:00	2578242	14861	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004898	PHOENIX	NORMAL OPERATION		Error No 2118: Bus Error / Inter-bus Failure	Inter-bus failure	Normally running time	SVG168 top panel	AO module malfunctioning	R.Aravindh R.Muthukumar	changed the AO module	1 - no	After replaced the AO module turbine running with normal operation.	Applied	Wtg stopped due to error no:2118 inter bus failure.We Checked additional alarm and warning in HMI log displayed 3.18, And found AO module was continuously malfunction in bus system.So we replaced it by new one then restart the wtg.	Wtg due to stop we are attend and found check the AO module failure condition.so replaced new one then start the WTG.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	DSC_0089.jpg AO module
CIR-10000595	100260861	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-045	0.85	65	Standard	ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	11/08/2014	402379461	31/05/2016	322-Anemometer error	Selvan S.	1404	1439	31/05/2016 14:55:00	31/05/2016 13:35:00	2175319	14780	CONTROL SYSTEM	NACELLE INSTRUMENTATION SYSTEM	GP004894	Thies	NORMAL OPERATION		Error No :322. Anemometer error occurred	Error No :322. Anemometer	Running time	Loc no:SVG139	continuous operation, material defect	R.Muthukumar	changed the CNT module	1-No	Continuous operation, material defective	Applied	Error No :322. Anemometer error occurred. Checked and found Wind speed showing Zero in display. | So we checked the Anemometer connection found ok,CNT Module malfunctioning | We found CNT module Failure confirmed, so replaced the new one module then start the WTG	Frequent operation,Material problem Short circuit, Loose connection.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	20160607_083450.jpg CNT module
CIR-10000562	100261281	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-093	0.85	65	Reinforced	ABB type C	4630879	Hansen	EH806A-001/CM0117	High Temperature	STD+	Standard	06/08/2014	402349047	29/04/2016	2118-Interbus bus error	Selvan S.	1404	1439	29/04/2016 17:08:00	29/04/2016 15:40:00	1901347	14282	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP004895	PHOENIX	NORMAL OPERATION		Error No 2118: Bus Error / Interbus Failure	Bus Error Inter-bus Failure	Running time	Loc No:SVG143	Continuous Operation,Grid fluctuation	R.Muthukumar R.Sethu	Replaced by new one RTD module.	1- No	Continuous Operation,Grid fluctuation and Environmental weather change.	Applied	Wtg due to stop We checked digital input, we are attend the found PLC displayed CTRL code 3.11. We found Temp RTD module Failure confirmed. Replaced by new one module.	After replaced the RTD module turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	20160519_142222.jpg 2 PAC RTD MODULE
CIR-10000569	100261281	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-093	0.85	65	Reinforced	ABB type C	4630879	Hansen	EH806A-001/CM0117	High Temperature	STD+	Standard	06/08/2014	402355119	06/05/2016	2118-Interbus bus error	Selvan S.	1404	1439	06/05/2016 15:35:00	06/05/2016 14:43:00	1919340	14447	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP004895	PHOENIX	NORMAL OPERATION		Wtg stopped due to Error no:2118 Inter bus failure error.	2118: inter bus failure error	Normal operation time	Nacelle Top cabinet panel	Frequent operation	D.Manoj R.Muthukumar	Changed the Temp 2 RTD module	1-No	Frequent operation,Material problem Short circuit, Loose connection.	Applied	Wtg stopped due to error no:2118 Interbus error. We check and found PLC display it shows 3.11 error. | We found Temp 2 RTD module Failure confirmed. | New one Temp 2 RTD module replaced , then start the WTG	Turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	Temp 2 RTD.JPG Temp 2 RTD module
CIR-10000663	100261269	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-086	0.85	65	Reinforced	ABB type C	4630879	Hansen	EH806A-001/CM0117	High Temperature	STD+	Standard	07/08/2014	402387830	07/06/2016	3239-Pulse pending encoder NOK	Selvan S.	1404	1439	07/06/2016 17:58:00	07/06/2016 15:42:00	2199022	15509	ELECTRICAL	GENERATOR SYSTEM	P390157, GP019625	Baumer Hubner, ABB	GRID FAILURE		After voltage fluctuation time error No 3239 Pulse pending encoder NOK occured	error No 3239 Pulse pending encoder NOK	After voltage fluctuation time	Loc no:SVG148	Grid Fluctuation,Material defective,Input voltage problem	D.Manoj	changed the new one encoder and rotor contactor	Each one no	Grid Fluctuation,Material defective,Input voltage problem	Applied	Checked the digital input | Rotor contactor feedback supply not came | we checked the encoder | ENCODER found not working properly | We found replace new one rotor contactor and GENERATOR ENCODER	After replaced the Encoder, rotor contactor turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	IMG_20160308_161206.jpg Encoder | IMG_20160108_120824.jpg 50 30 contactor | 50 30 contactor.jpg 50 30 contactor
CIR-10000563	100261323	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-099	0.85	65	Reinforced	ABB type C	4633323	Hansen	EH806A-001/CM0157	High Temperature	STD+	Standard	06/08/2014	402349051	29/04/2016	2118-Interbus bus error	Selvan S.	0	1439	29/04/2016 10:13:00	29/04/2016 08:50:00	2140516	14513	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004891	PHOENIX	GRID FAILURE		Bus Error Inter-bus Failure	2118 - Bus failure	Grid resuming time	LOC No:SVG178	continuous Operation	R.Aravindh R.Muthukumar	new one SEG module replaced.	1- No	This component was failure due to Continuous Operation,voltage fluctuation and material defect	Applied	Wtg stopped due to Error no:2118 Inter bus Error.When turbine running this error occurred.We see the alarms in HMI log it shows on 3.13. We have checked and found that SEG module was failure. So the SEG module was changed and WTG restarted.	After replaced the SEG module turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	DSCN1571.JPG SEG MODULE
CIR-10000403	100261317	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-089	0.85	65	Reinforced	ABB type C	4633323	Hansen	EH806A-001/CM0157	High Temperature	STD+	Standard	04/06/2014	402230744	08/01/2016	-0	Selvan S.	1404	1439	08/01/2016 11:09:00	08/01/2016 08:49:00	3282915	13584	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004897	PHOENIX	NORMAL OPERATION		WTG stopped due to 2118- Bus error inter bus fail	2118-Bus failure	durnig running time.	TOP panel	surge voltage	D.Mano, R.Aravindh	Change the AI (2 PAC ) module	1	Surge voltage, Continuous operation.	Applied	PLC displayed CTRL code 3.16, So we checked related connection While checking we found AI module (2 PAC) got failure it was replaced by new one.	Wtg due to stop we are attand and found check the PLC displayed code no 3.16, so we found change the AI (2 PAC) module failure condition.so replaced new one then start the WTG.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	AI module.jpg AI ( 2 PAC ) Module
CIR-10000425	100260942	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-051	0.85	65	Standard	ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	29/04/2014	402316502	29/03/2016	-0	Selvan S.	1404	1439	29/03/2016 23:39:00	29/03/2016 22:05:00	2880000	16113	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004975	PHOENIX	NORMAL OPERATION		Error No 2107. Initialization fail.error occurred	Error No 2107. Initialization fail.error occurred	Normally running time	LOC :SVG41 bottom cabinet	Failure during surge voltage, voltage fluctuation.	D.Manoj, R.Muthukumar R.Sethu	Replaced the new one PLC	1-No	After replaced the PLC module(RFC 430 ETH-IB) turbine running with normal operation.	Applied	During running time this error no:2107 Plc installation failure was occurred.We check and found Plc was failed.So we replaced by new one then program was upgraded.	After replaced the PLC module (RFC 430 ETH-IB) turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	PLC.jpg PLC
CIR-10000137	100260855	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-056	0.85	65	Standard	ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	29/06/2014	402224724	02/01/2016	2112-TOP supply failure	Selvan S.	1404	1425	02/01/2016 17:43:00	02/01/2016 14:28:00	2423482	13051	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP144138	Wiedmuller	NORMAL OPERATION	8951360000	Top Supply Failure error occurred	top supply failure	running time	bottom panel	Material defective.	power supply	digital input not coming so replaced.	one power supply	Material Defective.	Closed	check the digital input | power suply input signal not coming | so replaced new one power supply	Grigd fluctution time componet failure.-Field Engineer-Selvan S. | approved-Field Operations Manager-Sivakumar S. | BOP Auditing recommended-Phone Technical Support-Senthil M. | Top power supply failure mode analysis check with repair circuit team-Functionality Support Lead-Murugesan P. | Repair team requested for failure/repair data.-Functionality Support Specialist-Mayank | ok-Quality-Vijay Chinnaswamy	power supply.jpg
CIR-10000138	100260855	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-056	0.85	65	Standard	ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	29/06/2014	402224724	02/01/2016	-0	Selvan S.	1404	1425	02/01/2016 17:43:00	02/01/2016 14:28:00	2423482	13051	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP144138	Wiedmuller	NORMAL OPERATION	8951360000	reject the CIR									Deleted	reject the CIR
CIR-10000160	100260855	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-056	0.85	65	Standard	ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	29/06/2014	402224724	02/01/2016	2112-TOP supply failure	Selvan S.	1404	1425	02/01/2016 17:43:00	02/01/2016 14:28:00	2423482	13051	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP144138	WEIDMULLER	NORMAL OPERATION	unknown	2112 - Top Supply Failure error								Error occurred due to input voltage problem in circuits	Deleted	Wtg stopped | Check the Digital input | power supply input signal not coming | so replaced the new one power supply then start the WTG.
CIR-10000168	100260855	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-056	0.85	65	Standard	ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	29/06/2014	402224724	02/01/2016	2112-TOP supply failure	Selvan S.	0	1425	02/01/2016 17:43:00	02/01/2016 14:28:00	2423482	13051	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP144138	Wiedmuller	NORMAL OPERATION		24VDC Power Supply absence found during grid restore time								Grid fluctuation.	Closed	Wtg stopped | Check the alarm in display | We check the digital input. | power supply 24 v supply not coming. | we found power supply failure so replaced new one. | restart the m/c	pls approve-Field Engineer-Selvan S. | Approved-Field Operations Manager-Sivakumar S. | BOP Auditing recommanded-Phone Technical Support-Senthil M. | Attach relevant failure component picture-Functionality Support Lead-Murugesan P. | looks to be trial CIR-Quality-Vijay Chinnaswamy
CIR-10000577	100261145	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-027	0.85	65	Standard	ABB type C	4630534	Hansen	EH806A-001/CM0018	High Temperature	STD+	Standard	29/04/2014	402371332	19/05/2016	3236-Pulse Encoder NOK	Selvan S.	1404	1439	19/05/2016 08:11:00	19/05/2016 02:08:00	2795920	17175	ELECTRICAL	GENERATOR SYSTEM	P390157	Baumer Hubner	GRID FAILURE		After voltage fluctuation time error No 3236 Pulse Encoder NOK occured	error No 3236 Pulse Encoder NOK occured	After voltage fluctuation time	LOC No:SVG103	Voltage fluctuation , continuous operation.	R.Aravind D.Manoj R.Muthukumar	Change the Encoder	1-No	Continuous operation, grid fluctuation	Applied	Wtg due to stop We checked digital input, We checked GENERATOR ENCODER found not working properly | We found GENERATOR ENCODER Failure confirmed, so replaced the new one ENCODER,	After replaced the Encoder turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	IMG_20160308_161230.jpg ENCODER
CIR-10000662	100261263	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-080	0.85	65	Reinforced	ABB type C	4630879	Hansen	EH806A-001/CM0117	High Temperature	STD+	Standard	04/06/2014	402387827	07/06/2016	2118-Interbus bus error	Selvan S.	1404	1439	07/06/2016 19:29:00	07/06/2016 18:07:00	2860108	17095	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004895	PHOENIX	GRID FAILURE		Error No 2118, BUS error - INTER BUS failure error occurred	Error No 2118, BUS error - INTERBUS failure	Grid resuming time	Loc no:SVG168	voltage fluctuation, continuous operation	R.Muthukumar D.Manoj	Change the RTD module	1 - No	voltage fluctuation, continuous operation	Applied	Wtg due to stop We checked digital input, While inspection we found RTD module LED was red indication occurred then conclude RTD module failure. so replaced the new one Temperature module, then start the WTG.	replaced the new one module wtg operation normal-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	20160519_142222.jpg RTD module
CIR-10000664	100261265	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-079	0.85	65	Reinforced	ABB type C	4630879	Hansen	EH806A-001/CM0117	High Temperature	STD+	Standard	05/06/2014	402389478	08/06/2016	2118-Interbus bus error	Selvan S.	1404	1439	08/06/2016 12:20:00	08/06/2016 12:20:00	1919340	14447	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004895	Phoenix	NORMAL OPERATION		Error No 2118: Bus Error / Interbus Failure	Error No 2118: Bus Error / Interbus Failure	Normal operation time	Loc no:SVG131	its is show abnormal temperature reading	A.Satish R.Aravindh	Changed the Rtd module	1- no	its is show abnormal temperature reading	Applied	Wtg due to stop We checked digital input, we are attend the found PLC displyed CTRL code 3.11 | While inspection we found RTD module LED was red indication occurred then conclude RTD module failure then replaced the new one	After replaced the Module turbine with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	20160519_142222.jpg 2 PAC RTD module
CIR-10000685	100261282	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-092	0.85	65	Reinforced	ABB type C	4630879	Hansen	EH806A-001/CM0117	High Temperature	STD+	Standard	07/06/2014	402391354	12/06/2016	2118-Interbus bus error	Selvan S.	1404	1439	12/06/2016 17:07:00	12/06/2016 16:23:00	2848148	16561	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004895	Phoenix	NORMAL OPERATION		Error No 2118: Bus Error / Interbus Failure	Error No 2118: Bus Error / Interbus Failure	Normal operation time	Loc No:SVG97	Continuous Operation,voltage fluctuation and material defect.	R.Sethu, D.Manoj, R.Muthukumar	Changed the new one 2 RTD temp module	1- No	Continuous Operation,voltage fluctuation and material defect.	Applied	Wtg due to stop We checked digital input, we are attend the found PLC displayed CTRL code 3.11. We found Temp 2 RTD module Failure confirmed, New one Temp 2 RTD module replaced , then start the WTG.	Module replaced after turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	20160519_142222.jpg Temp 2 RTD Module
CIR-10000405	100260899	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-054	0.85	65	Standard	ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	29/04/2014	402254846	02/02/2016	-0	Selvan S.	1404	0	02/02/2016 13:17:00	02/02/2016 06:33:00	2434721	15257	MECHANICAL	GEARBOX SYSTEM	P370250	Gamesa	NORMAL OPERATION		WTG stopped due to 2118- Bus error interbus failure.								maybe problem for Voltage fluctuation	Applied	Wtg due to stop We checked digital input, we are attend the found PLC displyed CTRL code 3.15. We found communications RS485 module Failure confirmed.	Wtg due to stop we are attend and found check the RS285 module failure condition.so replaced new one then start the WTG.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	IMG_20160308_161143.jpg RS 285 Module
CIR-10000573	100261315	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-091	0.85	65	Standard	ABB type C	4633323	Hansen	EH806A-001/CM0157	High Temperature	STD+	Standard	05/06/2014	402363820	12/05/2016	2118-Interbus bus error	Selvan S.	1404	1439	12/05/2016 01:29:00	12/05/2016 00:20:00	2969075	16324	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004896	PHOENIX	NORMAL OPERATION		Error No 2118: Bus Error / Inter bus Failure	2118: Bus Error / Interbus Failure	Running time	top panel	Continuous Operation,voltage fluctuation and material defect.	R.Muthukumar D.manoj	Change the new module	1-No	Frequent operation,Material problem Short circuit, Loose connection	Applied	Wtg due to stop We checked digital input, we are attend the found PLC displyed CTRL code 3.15. We found RS 485/422 PRO PAC module Failure confirmed | We found RS 485/422 PRO PAC module Failure confirmed, so replaced the new one module then start the WTG	After replaced the module turbine running with normal operation-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	IMG_20160308_161143.jpg RS 485/422 PRO PAC module
CIR-10000436	100261120	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-048	0.85	65	Standard	ABB type C	4630534	Hansen	EH806A-001/CM0018	High Temperature	STD+	Standard	29/04/2014	402341624	19/04/2016	2118-Interbus bus error	Selvan S.	1404	1439	19/04/2016 19:40:00	19/04/2016 18:13:00	3155572	16538	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP004896	PHOENIX	NORMAL OPERATION		Error No 2118: Bus Error / Inter-bus Failure	Error No 2118: Bus Error / Inter-bus Failure	During running time	Loc no:SVG33 top panel	malfunctioning the module	D.Manoj, R.Muthukumar	Changed the New one module	1- No	This RS485/422 module failure due to Continuous Operation,Grid fluctuation and Environmental weather change.	Applied	Wtg stopped due to error no:2118 inter bus failure.We Checked additional alarm and warning in HMI log. And found RS485/422 module was continuously malfunction in bus system.So we replaced it by new one then restart the wtg.	After replaced the RS485/422 module turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	IMG_20160308_161143.jpg RS485/422 module
CIR-10000404	100261317	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-089	0.85	65	Reinforced	ABB type C	4633323	Hansen	EH806A-001/CM0157	High Temperature	STD+	Standard	04/06/2014	402230744	08/01/2016	-0	Selvan S.	1404	1439	08/01/2016 11:09:00	08/01/2016 08:49:00	3282915	13584	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004897	PHOENIX	NORMAL OPERATION		Error No 401: Low P(Gearbox) Error occured	401: Low P(Gearbox)	Loc :SVG88	gearbox	Hose leakage	D.Manoj, R.Aravindh, R.Muthukumar	One Hose and one pressure switch replaced and 20lit oil top up.	1 hose and pressure switch,20 lit oil	Continuous operation, over heat.	Applied	Stop the machine | Check the HMI log file | Check the digital input | OIL leakage inside and outside the tower ring | Gearbox to Radiator hose damaged | replaced the new one hose | Pressure switch one replaced. | Top up the 20Lit oil and restart the M/c	Wtg due to stop we are attend and found check the Hose and pressure switch failure condition.so replaced each one then start the WTG.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	pressure switch.jpg Pressure switch | hose.jpg PIGTAIL PRESSURE PUMP
CIR-10000407	100261317	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-089	0.85	65	Reinforced	ABB type C	4633323	Hansen	EH806A-001/CM0157	High Temperature	STD+	Standard	04/06/2014	402230744	08/01/2016	-0	Selvan S.	1404	1439	08/01/2016 11:09:00	08/01/2016 08:49:00	3282915	13584	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004897	PHOENIX	NORMAL OPERATION
CIR-10000424	100261317	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-089	0.85	65	Reinforced	ABB type C	4633323	Hansen	EH806A-001/CM0157	High Temperature	STD+	Standard	04/06/2014		23/03/2016	2118-Interbus bus error	Selvan S.	1404	1439	24/03/2016 00:40:00	23/03/2016 23:00:00	3282915	13584	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP082782	PHOENIX	NORMAL OPERATION		Error No 2118. Bus error Inter-bus fail error occurred.	Bus error interbus failure	normal running time	SVG145 (Top cabinet )	Malfunctioning the module, surge voltage	D.Manoj R.Aravindh M.Muthu	Change the new one RTD module	1- no	After replaced the RTD module turbine running with normal operation.	Applied	Stop the machine | check the HMI log | We see the alarms in HMI log it shows on 3.11 | So we found RTD module got malfunctioning , replaced the good one and restart the m/c	After replaced the Temp RTD module turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	IMG_20160308_160905.jpg Temp RTD module
CIR-10000684	100261264	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-084	0.85	65	Reinforced	ABB type C	4630879	Hansen	EH806A-001/CM0117	High Temperature	STD+	Standard	04/06/2014	402389486	09/06/2016	-0	Selvan S.	1404	1439	09/06/2016 15:43:00	09/06/2016 11:42:00	2864084	17106	MECHANICAL	GEARBOX SYSTEM	GP005720	OILTECH	NORMAL OPERATION		Warning error Gearbox pump thermal. Error no:421 ( rectification work )	421- warning error Gearbox pump thermal	Running time	Loc No: SVG16	Continuous operation	D.Manoj,R.Muthukumar, R.Aravindh	Changed the main pump	1 - No	Continuous Operation, manufacture defect.	Applied	WTG manually stopped due to warning error Gearbox pump thermal. Error no:421 rectifying work | We checked digital input, we are attend the found motor connection | Checking time we found motor good condition, | Main pump got failure, so replaced the new one Pump.	Online motor pump replaced after turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	online motor.jpg Online motor pump.
CIR-10000422	100261263	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-080	0.85	65	Reinforced	ABB type C	4630879	Hansen	EH806A-001/CM0117	High Temperature	STD+	Standard	04/06/2014	402296912	02/03/2016	3236-Pulse Encoder NOK	Selvan S.	1404	1439	02/03/2016 23:29:00	02/03/2016 19:07:00	2571201	14796	ELECTRICAL	GENERATOR SYSTEM	P390157	Baumer Hubner	NORMAL OPERATION		Grid resume time error No 3236 Pulse Encoder NOK occured	pulse encoder NOK	Grid resume time	SVG168	This encoder failure due to Continuous Operation and material defective.	R.Aravindh R.Muthukumar	Change the new one Encoder	!-no	After replaced by new Encoder turbine running with normal operation.	Applied	wtg stopped due to 3236 - pulse encoder NOK | check the digital input | We Checked additional alarm and warning in HMI log | encoder RPM measuring in wrongly so we found changed the new Encoder	After replaced the Encoder turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	IMG_20160308_161230.jpg Encoder
CIR-10000441	100261126	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-035	0.85	65	Standard	ABB type C	4630534	Hansen	EH806A-001/CM0018	High Temperature	STD+	Standard	29/04/2014	402326355	05/04/2016	-0	Selvan S.	1404	1439	05/04/2016 15:59:00	05/04/2016 15:59:00	3114953	15969	CONTROL SYSTEM	NACELLE INSTRUMENTATION SYSTEM	GP119771		NORMAL OPERATION		Error No :313. Very High Misalignment error occurred	Error No :313. Very High Misalignment	Running time	Loc no:SVG50 ( nacelle outside )	Continuous operation, loose connection.	D.Manoj, R.Muthukumar,	Changed the new one anemometer	1-No	Continuous operation, Material problem,Loose connection.	Applied	Checked and found Wind speed showing Zero in display.So we checked the Anemometer connection and found Anemometer Jammed condition. So we confirmed the Anemometer was failed, it was be replaced with new one.	Turbine running with normal operation-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	AI MODULE.jpg Thies Anemometer | 20160519_163245.jpg thies anemometer
CIR-10000191	100261273	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-075	0.85	65	Reinforced	ABB type C	4630879	Hansen	EH806A-001/CM0117	High Temperature	STD+	Standard	29/04/2014	402276230	22/02/2016	-0	Selvan S.	1404	1425	22/02/2016 17:43:00	22/02/2016 15:40:00	2469969	14820	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP082783	Phoenix	NORMAL OPERATION	7000516556	Wtg stopped due to Bus error inter bus failure.	bus interbus failure	running time	top panel	poor quality	D.manoj R.Aravindh R.Sethu	Plc displayed code 3.11	one module	grid fluctuation in more time	Assigned	Stopped the machine | checked the alarm log | we check the PLC ckt | PLC displayed CTRL code 3.11 | we found checked the temperature module | Temp module got failure | Replace the new one	Pls Aprove-Field Engineer-Selvan S. | Approved-Field Operations Manager-Sivakumar S. | Shield Earthing must checked-Phone Technical Support-Senthil M. | RCA to be done based on failure rate-Functionality Support Lead-Shankar Anand R.	Temp RTD module.jpg
CIR-10000196	100261273	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-075	0.85	65	Reinforced	ABB type C	4630879	Hansen	EH806A-001/CM0117	High Temperature	STD+	Standard	29/04/2014	402276230	22/02/2016	-0	Selvan S.	1404	1425	22/02/2016 17:43:00	22/02/2016 15:40:00	2469969	14820	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP082783	Phoenix	NORMAL OPERATION	7000516556	Wtg stopped due to Bus error inter bus failure.	Error no:2118 Bus Error / interbus fail	During Running time this error was occurred.	SVG94 Top panel	Continuous operation,Grid fluctuation and Material defect.	D.Manoj R.muthukumar M.muthu	Replaced by the new one RTD module.	1 - no	grid fluctuation		we reached the m/c | check the alarm log | check the digital input | PLC displayed CTRL 3.11 | We found temp RTD module failure conform | So replace the new one Module		Temp RTD module.jpg
CIR-10000197	100261273	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-075	0.85	65	Reinforced	ABB type C	4630879	Hansen	EH806A-001/CM0117	High Temperature	STD+	Standard	29/04/2014	402276230	22/02/2016	-0	Selvan S.	1404	1425	22/02/2016 17:43:00	22/02/2016 15:40:00	2469969	14820	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP082783	Phoenix	NORMAL OPERATION	7000516556
CIR-10000576	100261002	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-071	0.85	65	Standard	ABB type C	4623693	Rexroth	737000001795	High Temperature	STD+	Standard	29/04/2014	402371232	16/05/2016	2118-Interbus bus error	Selvan S.	1404	1439	16/05/2016 04:40:00	16/05/2016 03:18:00	3011228	17053	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP082783	PHOENIX	GRID FAILURE		Error No 2118. Bus error Inter-bus fail error occurred.	Error No 2118. Bus error Inter bus fail error occurred.	Grid Resuming time	Loc no:SVG90	abnormal temperature reading	R.Aravind D.Manoj R.Muthukumar	Change the Temp module	1-No	its is show abnormal temperature reading	Applied	While inspection we found RTD module LED was red indication occurred then conclude RTD module failure then replaced the new one wtg operation normal	Machine running normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	IMG_20160308_160905.jpg Temp module
CIR-10000561	100260863	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-046	0.85	65	Standard	ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	29/04/2014	501021683	26/04/2016	-0	Selvan S.	1404	1439	26/04/2016 19:19:00	26/04/2016 18:15:00	2771012	16381	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP019604	Gamesa	NORMAL OPERATION		During maintenance time power supply failure.	Battery power supply Failure	Maintenance time	Loc No:SVG138	Continuous Operation,voltage fluctuation and material defect.	R.muthukumar R.Aravindh	replaced the new one battery	1-No	This component was failure due to Continuous Operation,voltage fluctuation and material defect.	Applied	Check the digital input | checked the related connections and found Brake battery unit voltage was dipped condition | So we replaced by new spare.	After replaced the Brake power supply turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	20160519_163410.jpg Brake power supply
CIR-10000431	100261120	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-048	0.85	65	Standard	ABB type C	4630534	Hansen	EH806A-001/CM0018	High Temperature	STD+	Standard	29/04/2014	402326391	06/04/2016	402-Gearbox oil level low	Selvan S.	1404	1439	07/04/2016 01:22:00	06/04/2016 23:44:00	3128948	16232	MECHANICAL	GEARBOX SYSTEM	GP082783	PHOENIX	NORMAL OPERATION		Error No :404. High T ( Gearbox Bearing ) error occurred	Error no:404 High T ( Gearbox Bearing )	During running time	SVG33 Gearbox	Temp rtd module was malfunctioning	D.Manoj, R.Aravindh,	Changed the Temp RTD module	1-no	After replaced the Temp module turbine running with normal operation.	Applied	Wtg due to stop for Gearbox bearing temp high | check the HMI log warnings and alarms | check the gearbox temperature | we checked the Gearbox bearing sensor found normal condition | Checked the gearbox bearing cover temperature is normal. | RTD module is malfunctioning, So we confirmed the Temp module was failure , change the new one Temp RTD module, then start the m/c .	After replaced by new one Temp RTD module turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	IMG_20160308_160905.jpg Temp RTD module
CIR-10000560	100261120	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-048	0.85	65	Standard	ABB type C	4630534	Hansen	EH806A-001/CM0018	High Temperature	STD+	Standard	29/04/2014	402341617	22/04/2016	113-Yaw motors thermomagnetic relay failure	Selvan S.	1404	1439	22/04/2016 16:41:00	22/04/2016 12:44:00	1603119	10580	ELECTRICAL	YAW SYSTEM	GP004261, GP004262	Phoenix	NORMAL OPERATION		Wtg stopped due to error no:113 Yaw motors thermomagnetic relay failure.	Error no:113 Yaw motors thermomagnetic relay failure	Running time	Loc no : SVG177	Surge voltage, Manufacture Defect	D.Manoj R.Muthukumar	Changed the new one relay and relay base.	Each one no's	Continuous operation, surge voltage	Applied	We Checked additional alarm and warning in HMI log. And found yaw motor feedback signal is not coming, checked the related connections and checked the relay with base, found relay got failure, replace the new one relay with base.	After replaced the Relay and relay base turbine with normal operation-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	Relay with base.jpg Relay base
CIR-10000412	100261122	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-034	0.85	65	Standard	ABB type C	4630534	Hansen	EH806A-001/CM0018	High Temperature	STD+	Standard	29/04/2014	402276228	22/02/2016	2118-Interbus bus error	Selvan S.	1404	1439	22/02/2016 17:43:00	22/02/2016 16:10:00	2641820	15217	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004898	PHOENIX	NORMAL OPERATION		Error No 2118. Bus error Inter-bus fail								Error occurred due to input voltage problem in circuits	Applied	Wtg due to stop we are attend and found PLC displayed CTRL code 3.18. We found AO module failure condition.so replaced new one then start the WTG.	Wtg due to stop we are attend and found check the AO module failure condition.so replaced new one then start the WTG.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	DSC_0089.jpg AO module
CIR-10000434	100261136	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-024	0.85	65	Standard	ABB type C	4630534	Hansen	EH806A-001/CM0018	High Temperature	STD+	Standard	29/04/2014	402336019	11/04/2016	-0	Selvan S.	1404	1439	12/04/2016 02:23:00	11/04/2016 21:44:00	2783962	16440	MECHANICAL	YAW SYSTEM	109109		NORMAL OPERATION		WTG stopped due to 114 low yaw brake pressure.	Error no:114 low yaw brake pressure	During running time	Loc :SVG123, Yaw manifold	Continuous operation	D.Manoj, A.Sathish, R.Muthukumar, R.Sethu	Changed the new one Solenoid valve.	1 - No	Continuous operation, loose connection.	Applied	Stopped the m/c. | Check the HMI log alarm and warning list. | checked the digital input. | We checked the digital input and check the yaw brake pressure, pressure is not increased we found check the yaw related electrical circuits and solenoid valves supply. | We found Solenoid valve got failure. So it has been replaced with new one.	After replaced the Solenoid valve turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	109109.jpg Solenoid valve. CVUA-6-PDN-3-MUH
CIR-10000597	100261136	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-024	0.85	65	Standard	ABB type C	4630534	Hansen	EH806A-001/CM0018	High Temperature	STD+	Standard	29/04/2014	402386531	04/06/2016	-0	Selvan S.	1404	1439	04/06/2016 14:13:00	04/06/2016 14:13:00	2974533	17683	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP082783	PHOENIX	NORMAL OPERATION		Error No 2106, Temp. measurement module fail error occurred	Error No 2106, Temp. measurement module failure	Running time	Loc no:SVG123	Malfunctioning	D.Manoj R.Aravindh	change the new RTD module	1-no	Material problem,Loose connection Due to Heat,Grid Fluctuation	Applied	Wtg due to stop We checked digital input, While inspection we found RTD module LED was red indication occurred then conclude RTD module failure, so replaced the new one Temperature module, then start the WTG.	turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	IMG_20160308_160905.jpg Temp RTD Module
CIR-10000559	100260862	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-002	0.85	65	Standard	ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	29/04/2014	402336443	19/04/2016	410-OGS	Selvan S.	1404	1439	19/04/2016 10:49:00	19/04/2016 07:56:00	2514135	16566	ELECTRICAL	NACELLE AND ROTOR THERMAL CONDITIONING SYSTEM	GP004888	PHOENIX	NORMAL OPERATION		Wtg during running time OGS error occurred.	OGS	Running time	LOC. No.SVG119	Continuous operation, material defect	D.Manoj R.Muthukumar	Change the new one (IBS IL 24 BK-LK-PAC INTERBUS BUS COUPLER ) module.	1-no	may be problem for CAB module communication port.	Applied	So we checked related connection While checking we found CAB module got failure it was replaced by new one.	After replaced the interbus coupler module turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	DSCN1555.JPG IBS IL 24 BK-LK-PAC INTERBUS BUS COUPLER
CIR-10000505	100260693	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-013	0.85	74		ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	21/03/2014	402344954	22/04/2016	-0	Ram Lakshmanan MP	1386	1439	22/04/2016 04:22:00	22/04/2016 03:05:00	3318714	17548	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP019603		GRID FAILURE		PLC Inizilation Fail	capsitor	POWER FAIL	BRG 511	FAILURE	RAMLAKSHMANAN,MUTHUKUMAR,ARUNKUMAR	capacitor failure so replaced new one	1		Applied	we are attend and check the capacitor failure so replaced new one.	Wtg due to stop we are attend and check the capacitor failure so replaced new one.-Field Engineer-Ram Lakshmanan MP | -Field Operations Manager-Ravibala Suresh S.
CIR-10000506	100260693	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-013	0.85	74		ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	21/03/2014	402344954	22/04/2016	-0	Ram Lakshmanan MP	1386	1439	22/04/2016 04:22:00	22/04/2016 03:05:00	3318714	17548	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004888	PHONEICX	GRID FAILURE		PLC Inizilation Fail	capmodule	GRID FAILURE	BRG 511	FAILURE	RAMLAKSHMANAN	PLC show 3.0 error check the OFC cable tightness we found cab module failure. replace new one	1		Applied	we are attend and check the PLC show 3.0 error check the OFC cable tightness we found cab module failure. replace new one then start the WTG.	we are attend and check the time PLC show 3.0 error check the OFC cable tightness we found cab module failure. replace new one then start the WTG.-Field Engineer-Ram Lakshmanan MP | -Field Operations Manager-Ravibala Suresh S.
CIR-10000608	100260708	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-019	0.85	74		ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	15/03/2014	402355640	03/05/2016	-0	Ram Lakshmanan MP	1386	1425	03/05/2016 13:53:35	03/05/2016 13:09:35	3918761	18456	ELECTRICAL	ELECTRICAL CABINET SYSTEM	REL0068		GRID FAILURE		Initialization fail	TIMER	OPERATION	BRG 535	FAILURE	RAM LAKSHMANAN,MUTHUPANDI	KR13A timer was failure so replaced	1		Applied	we are attend and found KR13A timer was failure so replaced new one. Then wtg start.	we are attend and found KR13A timer was failure so replaced new one. Then wtg start. -Field Engineer-Ram Lakshmanan MP | -Field Operations Manager-Ravibala Suresh S.
CIR-10000041	100261530	CLEAN WIND POWER (MANVI) PVT. LTD	KAVITAL-G9X	WF-IN-010-1257-Y0-A-013-MDN	2	90.2	LM	Cantarey	479387	Hansen	EH806A-031/CM0101	Standard+	STD+	Standard	14/03/2015	445760	01/02/2016	-0	Raghu S.	1387	1425	01/02/2016 19:26:00	01/02/2016 10:30:00	567898	500	ELECTRICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	gp09765	ABB	NORMAL OPERATION	475876979	There is pumping problem in HU	pumping problem	ovrervoltage	HU unit	S/S	raghu	reolace a motor	only one	pump may get failure, accumulator may get failure	Assigned	Stopped the machibe | contactor ok | 24v relay pok | mpcb ok | machine doesnt run | Contunity in motor is not ok	aprroval-Field Engineer-Raghu S. | Approved-Field Operations Manager-Sivakumar S. | closed-Phone Technical Support-Senthil M. | The precharge pressure to be checked for the accumulator-Functionality Support Lead-Anand A.P | -Quality-Vijay Chinnaswamy	20151226_142625.jpg | 20160206_143712.jpg | FIELD ALERT 064- 615 ACCELEROMETER VIBRATION ALARM IN G97 TOWER 104m& 90.3m TURBINES.pdf
CIR-10000204	100261532	CLEAN WIND POWER (MANVI) PVT. LTD	KAVITAL-G9X	WF-IN-010-1257-Y0-A-018-MDN	2	90.2	LM	Cantarey	801251183	Hansen	EH806A-031/CM0089	Standard+	STD+	Standard	15/03/2015	402313349	25/03/2016	-0	M.Nagaraja	1385	1425	26/03/2016 18:31:00	25/03/2016 07:10:00	0	8585	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	GP062758	glual	NORMAL OPERATION	FCE000429D	oil leaking from the Pitch actuator of Blade â€œCâ€ﾝ.	oil leak	during running	pitch cylinder	oil seal failure	hub	new on replaced	1	during long time operation oil seal failure	Closed	cleaning don | remove the old cylinder | cylinder shift from HUB | new one lifting | shifting to HUB | replace the new one | all related connection checked	cylinder replaced don at 26.03.16-Field Engineer-M.Nagaraja | completed-Field Operations Manager-S.Chellaperumal | Detailed RCA recomanded-Phone Technical Support-Senthil M. | Site to share more pictures and fill the attached checklist and send to HO-Functionality Support Lead-Anand A.P | RCA is in progress - in Week 18 the reinforced seal trial will be completed-Quality-Vijay Chinnaswamy | Closed-Functionality Support Lead-Anand A.P | Under 8D evolution-Quality-Vijay Chinnaswamy	Format Checklist leakages Cylinders Inspection R01.xls Checklist format to fill during any oil from pitch cylinder
CIR-10000445	100261132	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-026	0.85	65	Standard	ABB type C	4630534	Hansen	EH806A-001/CM0018	High Temperature	STD+	Standard	29/04/2014	402336023	14/04/2016	410-OGS	Selvan S.	1404	1439	15/04/2016 12:53:00	14/04/2016 12:53:00	3362453	16481	ELECTRICAL	GEARBOX SYSTEM	1094574	Gamesa	NORMAL OPERATION		WTG stopped due to 410 OGS	Error no:410 OGS	running time	Loc no:SVG60 Top panel.	Frequent operation	D.Manoj, R.Aravindh, A.Sathish	Change the Brake power supply	1-No	Frequent operation,Material problem Short circuit, Loose connection.	Applied	We checked the digital input, we found check the OGS relay and OGS sensors are good and values fine, Brake power supply failure conformed, We found Brake power supply got failure and changed the good one.	Turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	20160519_163410.jpg Brake power supply
CIR-10000575	100261132	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-026	0.85	65	Standard	ABB type C	4630534	Hansen	EH806A-001/CM0018	High Temperature	STD+	Standard	29/04/2014	402371233	16/05/2016	2118-Interbus bus error	Selvan S.	1404	1439	16/05/2016 19:20:00	16/05/2016 17:51:00	3493373	17225	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004898	PHOENIX	GRID FAILURE		Error No 2118: Bus Error / Inter bus Failure	Bus Error Inter bus Failure	Grid resume time	Loc No:SVG60 Top panel	Material problem,Loose connection Due to Heat,Grid Fluctuation.	R.Aravindh, R.Muthukumar	Changed the AO module	1 - No	Material problem,Loose connection Due to Heat,Grid Fluctuation.	Applied	Wtg due to stop We checked digital input, we are attend the found PLC displyed CTRL code 3.18. We found AO module Failure confirmed | We found AO module Failure confirmed, so replaced the new one module then start the WTG	turbine running with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	DSC_0089.jpg AO Module
CIR-10000034	100260878	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-019	0.85	65	Standard	ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	29/04/2014	44	17/02/2016	3211-SkiiP Error rotor inverter phase 3	Selvan S.	1404	1425	17/02/2016 12:30:00	17/02/2016 10:21:00	233300	15888	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	gp0123	abb	NORMAL OPERATION	1222	skip module	3211	normal operation	banal	4	skip module	5	6	skip	Deleted	machine stopped | check the digital input | check the cable | change the new one
CIR-10000421	100260860	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-004	0.85	65	Standard	ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	29/04/2014	402283001	27/02/2016	3415-Emergency circuit open	Selvan S.	1404	1439	27/02/2016 16:51:00	27/02/2016 15:55:00	2619985	15413	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004898	Phoenix	NORMAL OPERATION		Error No 3415. Emergency circuit open( Grid resume time )	Error No 3415. Emergency circuit open.	Grid resume time	top panel	malfunctioning the module	D.Manoj, V.Bala murugan M.Muthu	changed the AO module	1- no	module failure due to malfunctioning,Continuous Operation,Grid fluctuation.	Applied	Wtg stopped due to error no:3415 emergency circuit open | We Checked additional alarm and warning in HMI log | We checked digital input | HMI log it shows 3.18 | we checked and found AO module failure confirmed | Replace the new one module and restart the m/c	After replaced by new AO module turbine running with normal operation-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	DSC_0089.jpg AO module
CIR-10000695	100261432	Rayala Wind Power Company Private Limited	RAYALA	WF-IN-001-1481-Y1-A-008-MDN	2	90.2	LM	Cantarey	801251074	Hansen	EH806A-001/CM0243	Standard+	STD+	Standard	07/01/2015		12/06/2016	-0	Seenivasagan G.	1459	1425	12/06/2016 12:55:00	12/06/2016 12:48:00	5481715	12004	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP011681	AEG	NORMAL OPERATION	264510137108n	Top ups supply failure warning is occurred	ups failure	Normal running	Electrical panel	Grid fluctuation		replaced new ups	1 nos	it will created the after grid failure plc power will cut off immediate	Assigned	While inspection ups feedback was missing after we confirmed the ups failure	UPS System failure-Field Engineer-Seenivasagan G. | Please recommend preventive action-Field Operations Manager-SARAVANAN.S | FSL Comments Requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.	Ups N27.jpg
CIR-10000690	100261593	ANANDAPURA WIND POWER COMPANY	RAYALA	WF-IN-001-1481-Y1-A-011	2	90.2	LM	Cantarey	479412	Hansen	EH806A-031/CM0165	Standard+	STD+	Standard	19/05/2015		15/06/2016	-0	Seenivasagan G.	1459	1425	15/06/2016 20:40:00	15/06/2016 12:11:00	5397125	9023	ELECTRICAL	GENERATOR SYSTEM		LIFT	NORMAL OPERATION	986201	while inspection generator internal cooling motor winding was failure	generator motor failed	normal operation	generator cooling system	Grid fluctuation		find the motor winding failure	1 Nos	It will created increase generator winding temp	Assigned	While checked cooling motor winding Ohmic value and found winding failure replaced with new motor	516 generator winding temp high warning-Field Engineer-Seenivasagan G. | Preventive action is required-Field Operations Manager-SARAVANAN.S | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.	IMG_20160616_151341.jpg | EVENTS OF G97-150.xls
CIR-10000766	100261438	Rayala Wind Power Company Private Limited	RAYALA	WF-IN-001-1481-Y1-A-002-MDN	2	90.2	LM	ABB type C	4635466	Hansen	EH806A-031/CM0010	Standard+	STD+	Standard	27/11/2014		25/06/2016	-0	Sivasree Saravanan K.	1459	0	25/06/2016 17:48:00	25/06/2016 14:07:00	58987	11797	ELECTRICAL	GENERATOR SYSTEM		ABB	NORMAL OPERATION	4635466		Generator slip ring carbon brushes/holder burnout.	During running	Generator slip ring	Carbon brush was stuck between brush holder to slip ring drum	Service team	New brush holders/brushes replaced	Brush holder-2Nos Brushes - 22Nos	Slip-ring may get burnout due to heavy arc.		All the damaged carbon brushes/holders have removed. | Cleaned the slipring drum | Replaced new carbon holders with brushes. | Cheked all the carbon brush holder conditions found ok
CIR-10000298	100260556	Sri Murugarajendra Oil Industry Pvt Ltd	Chikkodi	WF-IN-010-0890-Y1-A-005	0.85	65	Standard	Gamesa wind Tianjin, China	801001202	Gamesa(Spain)	100390	High Temperature	STD+	Standard	27/08/2011	212	04/04/2016	2118-Interbus bus error	Arockiaraj D.	1373	1425	11/04/2016 16:12:00	04/04/2016 16:12:00	12	12	CONTROL SYSTEM	DRIVE TRAIN	12	21	GRID FAILURE	12212	adafds	aa	aa	aa	aa	aa	aa	saa	adasdsa
CIR-10000400	100260900	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-011	0.85	65	Standard	ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	29/04/2014		16/05/2016	3502-PLC Communication Error	Selvan S.	1404	1439	16/05/2016 06:01:00	16/05/2016 01:25:00	2734434	17430	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	50019	ABB	GRID FAILURE	3471522050809	PLC Communication Error ( Grid failure time ). KM013 Contactor failure in 13 turbines ( 230 V contactor for bottom panel supply )	PLC communication error	Grid failure time	Loc no:SVG27,SVG16,SVG17,SVG18,SVG19,SVG20,SVG22,SVG23,SVG25,SVG26,SVG15,SVG154. SVG48	short circuit the feeder 1 & 2 line.	R.Aravindh R.Sethu	changed the contactor.	13 ( contactor A16-30-10).	short circuit in Grid failure time	Applied	reached the m/c | Check the voltage | KM013 ( 230v contactor panel power supply got failure )	Grid failure time m/c component failure.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	IMG-20160516-WA0004.jpg contactor A16-30-10 | IMG-20160516-WA0002.jpg Coil melted pic
CIR-10000426	100261010	MYTRAH VAYU KRISHNA PVT LTD	SAVALSUNG	WF-IN-010-1193-Y0-A-074	0.85	65	Standard	ABB type C	4623693	Rexroth	737000001795	High Temperature	STD+	Standard	29/04/2014	402326118	04/04/2016	111-Max hydraulic unit pumping time	Selvan S.	1404	1439	04/04/2016 18:57:00	04/04/2016 12:05:00	2982490	16166	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	50758	Gamesa	NORMAL OPERATION		Error No 111: Max hydraulic unit pumping time error occured.	Error No 111: Max hydraulic unit pumping time error occured	During running time	loc no 155 HU tank inside	continuous operation, manufacture defect	D.Manoj R.Muthukumar R.Aravindh R.Sethu	Change the Metal hose	1-no	After replaced the metal hose turbine with normal operation.	Applied	Wtg stopped due to error no:111 Max hydraulic unit pumping time | Check the HMI log | Check the warning and alarm | HU Pressure not not developing | Tank Entire side oil leakage observed | remove the HU tank cover and metal hose got damaged condition | Replaced new one metal hose then restart the m/c	After replaced the Hose turbine with normal operation.-Field Engineer-Selvan S. | -Field Operations Manager-Sivakumar S.	IMG_20160108_121602.jpg metal hose
CIR-10000349	100260693	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-013	0.85	74		ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	21/03/2014	402344954	22/04/2016	-0	Ram Lakshmanan MP	1386	1425	22/04/2016 16:22:56	22/04/2016 15:05:56	3318714	17548	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP043936		GRID FAILURE		PLC Inizilation Fail	40amps fuse	operation	BRG 511	failure	ramlakshmanan	we check the 40A fuse failure replaced new one.	1		Applied	we are attend and check the 40A fuse replaced new one.	Wtg due to stop we are attend and check the 40A fuse failure replace new one then start the WTG. -Field Engineer-Ram Lakshmanan MP | -Field Operations Manager-Ravibala Suresh S.
CIR-10000251	100261032	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-042	0.85	65		Cantarey	801250605	Hansen	EH806A-001/LM0045	High Temperature	STD+	Standard	21/02/2014	402317551	25/03/2016	-0	Ram Lakshmanan MP	1386	1439	25/03/2016 23:51:00	25/03/2016 22:43:00	3171312	17594	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP043936		GRID FAILURE		Line Protection Triggered	40A FUSE	OPERATION	BRG 509	GRID FLUCTUATION	MUTHUPANDI	found 40A fuse 2nos failure then Replaced	2	GRID FLUCTUATION	Assigned	wtg stopped Due to line protection triggered. We are attend and found 40A fuse 2nos failure then Replaced new one wtg started .	wtg stopped Due to line protection triggered. We are attend and found 40A fuse 2nos failure then Replaced new one wtg started .-Field Engineer-Ram Lakshmanan MP | Failure-Field Operations Manager-Ravibala Suresh S. | BOP Auditing recommended-Phone Technical Support-Senthil M. | BOP fuse standardization is recommended-Functionality Support Lead-Murugesan P. | -Functionality Support Specialist-Selvamani K.	GP043936.jpg
CIR-10000252	100261032	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-042	0.85	65		Cantarey	801250605	Hansen	EH806A-001/LM0045	High Temperature	STD+	Standard	21/02/2014	402317551	25/03/2016	-0	Ram Lakshmanan MP	1386	1439	25/03/2016 23:51:00	25/03/2016 22:43:00	3171312	17594	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP019603	EPCOS	GRID FAILURE		Line Protection Triggered	capacitor	OPERATION	BRG 509	GRID FLUCTUATION	RAM,MUTHUKUMAR	REPLACED THE CAPACITOR	1	GRID FLUCTUATION	Assigned	wtg stopped Due to line protection triggered. We are attend and found capacitor 1no failure then Replaced new one wtg started .	capacitor 1no failure then Replaced new one-Field Engineer-Ram Lakshmanan MP | Failure-Field Operations Manager-Ravibala Suresh S. | BOP Auditing recommended-Phone Technical Support-Senthil M. | Type I Surge Arrester project recommended-Functionality Support Lead-Murugesan P. | -Functionality Support Specialist-Mayank
CIR-10000118	100260954	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-033	0.85	65		ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	21/02/2014	402309023	18/03/2016	-0	Arun Kumar K.	1386	1439	18/03/2016 13:21:00	18/03/2016 12:45:00	3484438	17521	ELECTRICAL	NACELLE INSTRUMENTATION SYSTEM	GP004896	phonix	NORMAL OPERATION		WTG Stop due to Inter bus Fail Error(2118)	MODULE	OPERATION	BRG 522	CONTINOUS OPERATION	ARUNKMAR	Replaced the RS485 module	1		Assigned	Wtg due to stop we are attend and found PLC diplay 3.17 error code so replaced the RS485 module then start the WTG.	Wtg due to stop we are attend and found PLC diplay 3.17 error code soreplaced the RS485 module then start the WTG.-Field Engineer-Arun Kumar K. | Module was failure or malfunction-Field Operations Manager-Ravibala Suresh S.	rs485.jpg
CIR-10000134	100260954	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-033	0.85	65		ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	21/02/2014		22/03/2016	-0	Ram Lakshmanan MP	1386	1439	23/03/2016 01:14:00	22/03/2016 23:56:00	3489305	17625	ELECTRICAL	HIGH SPEED SHAFT COUPLING SYSTEM	1094574	gamesa	NORMAL OPERATION		High brake temperature	brake power supply system	operation brake down	top panel	continuous operation	ramlakshmanan	we check the brake power supply system failure so replaced new one	1		Assigned	we check the brake power supply system failure so replaced new one	we check the brake power supply system failure so replaced new one-Field Engineer-Ram Lakshmanan MP | Failiure-Field Operations Manager-Ravibala Suresh S. | closed-Phone Technical Support-Senthil M. | Brake power suppl battery Proactive replacement recommended as per field alert-Functionality Support Lead-Murugesan P. | -Quality-Vijay Chinnaswamy	P_20160325_091758.jpg
CIR-10000099	100261425	Rayala Wind Power Company Private Limited	RAYALA	WF-IN-001-1481-Y1-A-005-MDN	2	90.2	LM	Cantarey	801251073	Hansen	EH806A-031/CM0004	Standard+	STD+	Standard	27/11/2014	402289615	29/02/2016	-0	Sivasree Saravanan K.	1420	1425	29/02/2016 19:35:00	29/02/2016 18:58:00	5304817	9317	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP011681	AGE	NORMAL OPERATION	(40)2624509127262d	UPS failed during normal operation. It is serviced UPS. It was worked for two day after replacing.	UPS was failure.	During normal operation	In ground control cabinet	It is serviced UPS and it may failed due to internal short circuit.	Service	We have to replaced the UPS with new one.	UPS:1 no's		Assigned	FM005 MCB was tripped due to failure of UPS. | burning smell observed inside of the UPS. it may occurred due to internal short circuit.	It is serviced UPS. It was worked for two day after replacing.-Field Engineer-Sivasree Saravanan K. | Need to takeup with supplier end. Now a days serviced UPS are supplied to site without any stickers.-Field Operations Manager-SARAVANAN.S | To be assign to Repair Center-Phone Technical Support-Senthil M. | Check FS057 Grounding cable wiring and it must be less 0.5 in Ground cabinet-Functionality Support Lead-Murugesan P. | this UPS failure issue need to be analyzed, since its a service UPS. kindly recall the failed UPS and carryout the analysis-Functionality Support Specialist-Venkatesh S | -Quality-Vijay Chinnaswamy	T6 UPS.jpg UPS | Sr.No.jpg Name plate details | Aqua Power+_20160310_162129.jpg UPS failed
CIR-10000609	100261030	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-044	0.85	65		Cantarey	801250605	Hansen	EH806A-001/LM0045	High Temperature	STD+	Standard	15/03/2014	402368027	07/05/2016	2118-Interbus bus error	Ram Lakshmanan MP	1386	1425	07/05/2016 17:04:35	07/05/2016 16:13:35	3446976	18543	ELECTRICAL	ELECTRICAL CABINET SYSTEM	REL0068		NORMAL OPERATION		Bus error-Interbus fail	Timer	OPERATION	BRG 548	failure	RAM,PANDI	KR330 Timer failure so replaced	1		Applied	We are attend and check KR330 Timer failure so replaced new one then wtg start.	We are attend and check KR330 Timer failure so replaced new one -Field Engineer-Ram Lakshmanan MP | -Field Operations Manager-Ravibala Suresh S.
CIR-10000729	100260929	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-007	0.85	74		ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	19/03/2014	402368015	19/05/2016	-0	Ram Lakshmanan MP	1386	1439	19/06/2016 10:47:00	19/06/2016 09:26:00	3321799	18170	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP095799		NORMAL OPERATION		HW Low DC-link voltage	chopped card	operation	BRG 518	HW Low DC-link voltage	ramlakshmanan, muthupandi	chopper card was failure so replaced new one	1		Applied	We checked chopped card was failure so replaced new one. Then wtg start.	due to HW Low DC-link voltage chopper card was failure so replaced new one-Field Engineer-Ram Lakshmanan MP | -Field Operations Manager-Ravibala Suresh S.
CIR-10000228	100260954	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-033	0.85	65		ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	21/02/2014	402309023	18/03/2016	-0	Ram Lakshmanan MP	1386	1425	18/03/2016 13:21:04	18/03/2016 12:45:04	3484091	17521	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004896	phoenic	NORMAL OPERATION		Wtg due to stopInterbus Failure	commnication module	operation	BRG 522	module failure	arunkumar	replaced the RS485 module	1		Closed	we are attend and found PLC diplay 3.17 error code so replaced the RS485 module then start the WTG.	Continuos(on and off) operating, Grid Fluctuation. Grid down for long time and Fluctuation.-Field Engineer-Ram Lakshmanan MP | RS485 module failure-Field Operations Manager-Ravibala Suresh S. | closed-Phone Technical Support-Senthil M. | Failure rate to be checked and if required we will do the RCA-Functionality Support Lead-Shankar Anand R. | park the issue-Quality-Vijay Chinnaswamy
CIR-10000283	100260954	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-033	0.85	65		ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	21/02/2014	402328149	09/04/2016	-0	Ram Lakshmanan MP	1386	1439	09/04/2016 21:41:00	09/04/2016 21:41:00	3532362	18041	ELECTRICAL	GENERATOR SYSTEM	P390157	encoder	NORMAL OPERATION		Encoder Slope Not Ok	Encoder	operation	BRG 522	FAILURE	ramlakshmanan	replaced the encoder generator	1	encoder failure	Assigned	Wtg due to stop we are attend and replaced the encoder generator then start the WTG.	Wtg due to stop we are attend and replaced the encoder generator then start the WTG.-Field Engineer-Ram Lakshmanan MP | Replaced encoder for testing now wtg under observation-Field Operations Manager-Ravibala Suresh S. | closed-Phone Technical Support-Senthil M. | -Functionality Support Lead-Shankar Anand R.	P390157.jpg
CIR-10000242	100260934	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-022	0.85	74		ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	16/03/2014		07/03/2016	-0	Ram Lakshmanan MP	1386	1439	07/03/2016 15:50:00	07/03/2016 15:40:00	3437717	16944	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL			NORMAL OPERATION		During 24 month service we abservered oil leak in pitch cylinder	pitch cylinder	operation	gear box BRG 539	leak	muthukumar			failure of pitch cylinder	Closed	need for suggestion	request for suggestion-Field Engineer-Ram Lakshmanan MP | Need your suggestion-Field Operations Manager-Ravibala Suresh S. | 8D ongoing-Phone Technical Support-Senthil M. | If the oil is more than 3.4 litres for 3 minutes during SIN test, then replace the pitch cylinder or do seal replacement. 8D is ongoing-Functionality Support Lead-Anand A.P | closed-Quality-Vijay Chinnaswamy	DSC01011 529.JPG | DSC01011 529.JPG
CIR-10000272	100260929	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-007	0.85	74		ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	19/03/2014	402317562	31/03/2016	-0	Ram Lakshmanan MP	1386	1439	31/03/2016 05:41:00	31/03/2016 05:08:00	3201521	16963	ELECTRICAL	ELECTRICAL CABINET SYSTEM	REL0068	finder	NORMAL OPERATION		HW DC Link voltage low	Timer	operation	BRG 518	continuous operation	ramlakshmanan	replace timer KR013A failure	1	continuous operation	Assigned	Wtg stop due to HW DC link voltage low we attend and found timer KR013A failure.so replace the new one then start the WTG.	Wtg stop due to HW DC link voltage low we attend and found timer KR013A failure.so replace the new one then start the WTG.-Field Engineer-Ram Lakshmanan MP | Timer module malfunction-Field Operations Manager-Ravibala Suresh S. | closed-Phone Technical Support-Senthil M. | Closed-Functionality Support Lead-Murugesan P. | -Quality-Vijay Chinnaswamy	P_20160324_124547.jpg
CIR-10000250	100261029	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-043	0.85	65		Cantarey	801250605	Hansen	EH806A-001/LM0045	High Temperature	STD+	Standard	15/03/2014	402309024	19/03/2016	-0	Ram Lakshmanan MP	1386	1439	19/03/2016 23:44:00	19/03/2016 23:33:00	23121811	17390	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004896	pheonics	NORMAL OPERATION		Interbus failure	module	operation break down	BRG 549	continuous operation	ramlakshmanan	replaced the RS485 module	1		Assigned	we are attend and found PLC diplay 3.17 error code so replaced the RS485 module then start the WTG.	we are attend and found PLC diplay 3.17 error code soreplaced the RS485 module then start the WTG.-Field Engineer-Ram Lakshmanan MP | RS485 module failure-Field Operations Manager-Ravibala Suresh S. | Surge protection to be ensured-Phone Technical Support-Senthil M. | -Functionality Support Lead-Shankar Anand R.	rs485.jpg
CIR-10000213	100260932	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-025	0.85	74		ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	15/03/2014		31/03/2016	-0	Ram Lakshmanan MP	1386	1425	31/03/2016 23:37:41	31/03/2016 23:10:00	3589904	17544	ELECTRICAL	ELECTRICAL CABINET SYSTEM	rel0068	finder	NORMAL OPERATION		Wtg due to stop due to the plc inizilation fail	timer	operation	coverter panal	contious operation	muthukumar	replace	1	Grid drop, Continuous operation	Assigned	we are attand and found the (KR013A) timer failure condition.so replaced new one then start the WTG.	Wtg due to stop we are attand and found check the (KR013A) timer failure condition.so replaced new one then start the WTG.-Field Engineer-Ram Lakshmanan MP | Tmer module Malfunction-Field Operations Manager-Ravibala Suresh S. | closed-Phone Technical Support-Senthil M. | Please confirm this is under project scope or diffent failure mode-Functionality Support Lead-Murugesan P. | -Functionality Support Specialist-Venkatesh S	REL0068 Timer.jpg
CIR-10000244	100260703	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-027	0.85	74		ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	15/03/2014		01/03/2016	-0	Ram Lakshmanan MP	1386	1439	01/03/2016 16:20:00	01/03/2016 16:10:00	3762876	196696	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL			NORMAL OPERATION		we abservered oil leak in pitch cylinder	pitch cylinder	operation	BRG 543	leak	muthukmar			failure pitch cylinder	Assigned	need suggestion	Need for suggestion-Field Engineer-Ram Lakshmanan MP | Need your suggestion-Field Operations Manager-Ravibala Suresh S. | detailed investigation recommanded-Phone Technical Support-Senthil M. | Gear oil leak from the pitch cylinder. Required endoscope inspection & further detailed investigation required-Functionality Support Lead-Anand A.P | -Functionality Support Specialist-Babu M.	DSC01013 543.JPG
CIR-10000113	100260933	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-024	0.85	74		ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	15/03/2014		04/03/2016	-0	Ram Lakshmanan MP	1386	1439	04/03/2016 10:05:00	04/03/2016 10:00:00	3628071	17006	MECHANICAL	TOWER SYSTEM			NORMAL OPERATION		chucker plate clamp damage	chucker plate clamp	operation	fourth shell	May be vibration,continuous operation	muthkumar	replace	1	May be vibration,continuous operation	Assigned	we are found that the fourth shell tower chucker plate clamp was damaged.	we are found that the fourth shell tower chucker plate clamp was damaged.-Field Engineer-Ram Lakshmanan MP | Clamp was low quality-Field Operations Manager-Ravibala Suresh S.	Avgl_zkpCc0L12Z-LTMeOzy7IuZHQzJo405f0zV_ZdvV.jpg
CIR-10000619	100260709	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-028	0.85	74		ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	16/03/2014	402367938	16/05/2016	3409-Line Protection Triggered	Ram Lakshmanan MP	1386	1439	16/05/2016 01:17:00	16/05/2016 00:22:00	3864980	18696	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP019603 -1 and GP043936-2	epcos	NORMAL OPERATION		Line Protection Triggered	surge arraster and 40A fuse	operation	BRG 536	failure	ram,pandi	40A fuse and capacitor failure so replaced new	GP019603 -1and GP043936-2		Applied	We are attend and check Line protection circuit and surge arrester circuit finally 40A fuse and capacitor failure so replaced new components. Then wtg start	We are attend and check Line protection circuit and surge arraster circuit finally 40A fuse and capacitor failure so replaced new compenents. Then wtg start-Field Engineer-Ram Lakshmanan MP | -Field Operations Manager-Ravibala Suresh S.	GP043936.jpg | GP019603.jpg
CIR-10000748	100260697	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-001	0.85	74		ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	14/03/2014	402372294	22/05/2016	-0	Ram Lakshmanan MP	1396	1425	22/05/2016 19:16:52	22/05/2016 17:05:52	3753134	18743	ELECTRICAL	COMPLETE ROTOR	p393405		NORMAL OPERATION		"OGS, High Brake Temp"	OGS	operation	BRG 531	OGS Rotor sensor failure	muthukumar , arunkumar	OGS Rotor sensor failure so replaced	1		Applied	We attend and replaced power supply and OGS Card for testing then finally we found the OGS Rotor sensor failure so replaced new one. Then wtg start "	We attend and replaced power supply and OGS Card for testing then finally we found the OGS Rotor sensor failure so replaced new one. Then wtg start " -Field Engineer-Ram Lakshmanan MP | -Field Operations Manager-Ravibala Suresh S.
CIR-10000136	100261029	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-043	0.85	65		Cantarey	801250605	Hansen	EH806A-001/LM0045	High Temperature	STD+	Standard	15/03/2014		23/03/2016	-0	Ram Lakshmanan MP	1386	1439	23/03/2016 22:45:00	23/03/2016 22:23:00	3125395	17477	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004894	phoenix	NORMAL OPERATION		Interbus fail	module	operation	top panel	failure	muthukumar	we are attend and found CNT module failure, so replace new one then start tha wtg"	1		Assigned	Wtg due to stop we are attend and found CNT module failure, so replace new one then start tha wtg"	we are attend and found CNT module failure, so replace new one-Field Engineer-Ram Lakshmanan MP | Module Failure-Field Operations Manager-Ravibala Suresh S. | Closed-Phone Technical Support-Senthil M. | Failure rate to be checked and if required we will do the RCA-Functionality Support Lead-Shankar Anand R. | -Quality-Vijay Chinnaswamy	GP004894.jpg
CIR-10000231	100261029	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-043	0.85	65		Cantarey	801250605	Hansen	EH806A-001/LM0045	High Temperature	STD+	Standard	15/03/2014			-0	Ram Lakshmanan MP	0	0	01/01/1900 00:00:00	01/01/1900 00:00:00	0	0	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM			NORMAL OPERATION		Interbus failure	timer	operation	BRG 549	failure	ramlakshmanan , muthukumar ,	.(KR330) timer failure so replaced new	1		Applied	we are attend and found check the timer connection.(KR330) timer failure condition.so replaced new one then start the WTG."	we are attend and found check the timer condition.(KR330) timer failure condition.so replaced new one-Field Engineer-Ram Lakshmanan MP | Please fill all the details-Field Operations Manager-Ravibala Suresh S. | completed-Field Engineer-Ram Lakshmanan MP | -Field Operations Manager-Ravibala Suresh S.	REL0068.jpg
CIR-10000611	100260947	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-035	0.85	65		ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	21/02/2014	402368017	11/05/2016	411-High brake temperature	Ram Lakshmanan MP	1386	1425	11/05/2016 19:48:35	11/05/2016 17:48:35	3584972	18892	ELECTRICAL	ELECTRICAL CABINET SYSTEM	1094574		NORMAL OPERATION		High brake temperature	brake power supply unit	operation	BRG 524	failure	muthukumar,arun	replaced new brake power suppiy unit	1		Applied	we are attend and replaced new brake power suppiy unit then start tha wtg then start.	we are attend and replaced new brake power suppiy unit then start tha wtg then start.-Field Engineer-Ram Lakshmanan MP | -Field Operations Manager-Ravibala Suresh S.
CIR-10000616	100260927	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-018	0.85	74		ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	15/03/2014	402368007	15/05/2016	410-OGS	Ram Lakshmanan MP	1386	1425	15/05/2016 18:18:35	15/05/2016 17:19:35	3965097	18800	ELECTRICAL	ELECTRICAL CABINET SYSTEM	REL0068	finder	NORMAL OPERATION		OGS	timer	operation	BRG 534	failure	ram,pandi	KR13a Timer got failure and replaced	1		Applied	WTG stopped due to OGS and found that KR13a Timer got failure and replaced with new one	WTG stopped due to OGS checked and found that KR330 Timer got failure and replaced with new one -Field Engineer-Ram Lakshmanan MP | -Field Operations Manager-Ravibala Suresh S.
CIR-10000348	100260931	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-026	0.85	74		ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	15/03/2014	402340372	20/04/2016	2112-TOP supply failure	Ram Lakshmanan MP	1386	1425	20/04/2016 22:21:56	20/04/2016 20:43:56	3982049	18029	ELECTRICAL	ELECTRICAL CABINET SYSTEM	REL0068	finder	GRID FAILURE		Top supply fail	timer	operation	BRG 542	failure	muthukumar	timer (KR330) was failure	1		Assigned	Wtg due to stop we are attend and check the top power supply unit and found top timer (KR330) was failure.so replaced new one then start the WTG.	we are attend and check the top power supply unit and found top timer (KR330) was failure.so replaced new one then start the WTG. -Field Engineer-Ram Lakshmanan MP | Timer Malfunction-Field Operations Manager-Ravibala Suresh S. | DM to be implemented pls call to Venkadesh - SE-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.
CIR-10000602	100260705	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-017	0.85	74		ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	21/02/2014	402344951	26/04/2016	-0	Ram Lakshmanan MP	1386	1425	26/04/2016 13:20:35	26/04/2016 12:38:35	3334763	18183	ELECTRICAL	NACELLE INSTRUMENTATION SYSTEM	9000601		NORMAL OPERATION		Manual stop for Power curve issue	Anemometer	operation	BRG 508	Power curve issue	ravi	the NRG Anemometer replaced	1		Applied	for Power curve issue NRG Anemometer replaced then start the WTG. Under abservation.	Manual stop for due to BRG508 Power curve issue. So replace the NRG Anemometer replaced then start the WTG. Under abservation. -Field Engineer-Ram Lakshmanan MP | -Field Operations Manager-Ravibala Suresh S.
CIR-10000666	100260429	Prabhu Spinning Mills (P) Ltd	PETHAPPAMPATTI	WF-IN-022-0853-Y0-A-010	0.85	65	Standard	Gamesa wind Tianjin, China	801001171	Gamesa(China)	602451	High Temperature	STD+	Standard	03/08/2011	402358121	10/05/2016	-0	Jeevanandam S.	1413	1439	10/05/2016 14:15:00	10/05/2016 11:35:00	8284620	38685	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP019520	Phoenix	NORMAL OPERATION		During New software Uploading work time								flash card failure	Applied	WTG manually stopped for new software uploading time flash card was failure so we replaced new one	WTG restarted normally -Field Engineer-Jeevanandam S. | -Field Operations Manager-Arumugam M.
CIR-10000026	100260465	Sudhan Spinning Mills (P) Ltd	PETHAPPAMPATTI	WF-IN-022-0853-Y0-A-006	0.85	65	Standard	Gamesa wind Tianjin, China	447597	Gamesa(China)	602502	High Temperature	STD+	Standard	03/08/2011	yet	17/02/2016	-0	Arumugam M.	1371	1373	15/02/2016 18:50:22	14/02/2016 17:15:22	7111180	35885	ELECTRICAL	TRANSFORMER SYSTEM	BOP000453	AMPTECH	GRID FAILURE	33/2691	After grid drop wtg stopped, while checking we found CTPT blasted in condition & photos are attached									Assigned	It wa replaced by new one	Failure ctpt was replaced by new one-Field Engineer-Arumugam M. | Ok Approved-Field Operations Manager-Sureshkumar K | closed-Phone Technical Support-Senthil M. | Please get arrange the root cause for this failure-Functionality Support Lead-Murugesan P. | -Functionality Support Specialist-Selvamani K.
CIR-10000486	100260474	Prabhu Spinning Mills (P) Ltd	PETHAPPAMPATTI	WF-IN-022-0853-Y0-A-007	0.85	65	Standard	Gamesa wind Tianjin, China	801001189	Gamesa(Spain)	100345	High Temperature	STD+	Standard	03/08/2011	402348051	29/04/2016	-0	Sorna Raja G.	1402	1439	29/04/2016 01:30:00	29/04/2016 00:00:00	7971610	38595	ELECTRICAL	ELECTRICAL CABINET SYSTEM	50105	SITOP	NORMAL OPERATION		WTG stopped due to the error 3409 - Line protection triggered								SITOP power supply unit failure	Applied	while checking we found SITOP power supply unit got failed so we replace the same with new one	WTG restarted normally -Field Engineer-Sorna Raja G. | -Field Operations Manager-Sureshkumar K
CIR-10000628	100260554	Sudhan Spinning Mills (P) Ltd	PETHAPPAMPATTI	WF-IN-022-0853-Y0-A-003	0.85	65	Standard	Gamesa wind Tianjin, China	801001280	Gamesa(Spain)	400895	High Temperature	STD+	Standard	10/08/2011	402361784	13/05/2016	-0	Venkatesan P.	1413	1439	13/05/2016 20:20:00	13/05/2016 18:30:00	7169940	37963	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP002750	Semikron	NORMAL OPERATION		WTG stopped due to 3210 - Skip Error Rotor Invertor Phase 2 error								Rotor skip failure	Applied	While running time FG005,FG008 handle was tripped condition we on that , Then error displayedwe cheecked the related circuit we confirm that rotor skip failure we changed new one	WTG restarted normally -Field Engineer-Venkatesan P. | -Field Operations Manager-Arumugam M.
CIR-10000307	100260695	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-015	0.85	74		ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	21/02/2014	402328140	05/04/2016	-0	Ram Lakshmanan MP	1386	1425	05/04/2016 14:22:06	05/04/2016 12:46:06	3446669	17691	ELECTRICAL	ELECTRICAL CABINET SYSTEM	REL0068	finder	NORMAL OPERATION		plc inizilation fail	timer	operation	BRG 510	failure	Arunkumar	Replaced new timer (KR330) failure	1	found timer (KR330) failure	Assigned	we are attend and found timer (KR330) failure so replaced new one	we are attend and found timer (KR330) failure so replaced new one then start the WTG. -Field Engineer-Ram Lakshmanan MP | Timer module malfunction-Field Operations Manager-Ravibala Suresh S. | Control solution requested by Electrical Team-Phone Technical Support-Senthil M. | Please check your project-Functionality Support Lead-Murugesan P. | -Functionality Support Specialist-Venkatesh S
CIR-10000603	100260698	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-004	0.85	74		ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	02/03/2014	402349147	28/04/2016	-0	Ram Lakshmanan MP	1386	1425	28/05/2016 13:33:35	28/05/2016 12:24:35	3769407	18441	ELECTRICAL	NACELLE INSTRUMENTATION SYSTEM	9000601		NORMAL OPERATION		Power curve issue.	Anemometer	operation	BRG 529	Power curve issue	muthukumar	NRG Anemometer replaced	1		Applied	for Power curve issue NRG Anemometer replaced	Manual stop for Power curve issue. the NRG Anemometer replaced then start the WTG. Under abservation.-Field Engineer-Ram Lakshmanan MP | -Field Operations Manager-Ravibala Suresh S.
CIR-10000382	100261448	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-035	2	90.2	LM	ABB type C	4635470	Hansen	EH806A-031/CM0018	Standard+	STD+	Standard	11/03/2015	402326005	07/04/2016	-0	Anand K.	1371	1373	07/04/2016 13:59:04	07/04/2016 12:57:00	5120196	9113	ELECTRICAL	YAW SYSTEM	GP022129	ABB	NORMAL OPERATION		HG contactor KM280 was failure.	HG contactor KM280	Normal operation	Top control panel rear side	Due to Continuous operation	K.ANAND,A.SIVANPERUMAL	To replace the new contactor	1	If we are not replace the contactor it may be affect the Hydralic system	Assigned	We have replaced the KM280 contactor.	Once we have replaced the contactor the next failure will take atleast 1 year -Field Engineer-Anand K. | KM 280 Contactor replaced-Field Operations Manager-Perumal P.V | FSL Comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Anand A.P
CIR-10000621	100260699	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-012	0.85	74		ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	14/03/2014	402353755	19/05/2016	-0	Ram Lakshmanan MP	1386	1439	19/05/2016 10:21:00	19/05/2016 08:19:00	3525688	18520	ELECTRICAL	ELECTRICAL CABINET SYSTEM	REL0068	finder	NORMAL OPERATION
CIR-10000622	100260699	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-012	0.85	74		ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	14/03/2014	402353755	19/05/2016	-0	Ram Lakshmanan MP	1386	1439	19/05/2016 10:21:00	19/05/2016 08:19:00	3525688	18520	ELECTRICAL	ELECTRICAL CABINET SYSTEM	REL0068	finder	NORMAL OPERATION		PLC initilization fail	Timer	operation	BRG 513	got failure	muthukumar,arun	KR13A Timer got failure and replaced	1		Applied	we attend and found that ground KR13A Timer got failure and replaced with new one	we attend and found that ground KR13A Timer got failure and replaced with new one-Field Engineer-Ram Lakshmanan MP | -Field Operations Manager-Ravibala Suresh S.	REL0068.jpg
CIR-10000606	100260954	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-033	0.85	65		ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	21/02/2014	402355614	02/05/2016	2112-TOP supply failure	Ram Lakshmanan MP	1386	1425	02/05/2016 16:05:35	02/05/2016 15:06:35	3589763	18567	ELECTRICAL	ELECTRICAL CABINET SYSTEM	REL0068		GRID FAILURE		Top supply failure	timer	operation	BRG 522	failure	ram,arun,muthukumar	replaced timer failure	1		Applied	we are attend and found that the timer failure and change new one then wtg start.	we are attend and found that the timer failure and change new one then wtg start. -Field Engineer-Ram Lakshmanan MP | -Field Operations Manager-Ravibala Suresh S.
CIR-10000749	100260952	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-034	0.85	65		ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	21/02/2014	402372297	23/05/2016	-0	Ram Lakshmanan MP	1396	1425	23/05/2016 18:18:52	23/05/2016 16:18:52	3685098	19149	ELECTRICAL	HIGH SPEED SHAFT COUPLING SYSTEM	1094574,rel0068,GP005798		GRID FAILURE		High Brake Temp	brake battery backup unit failure	grid resume	BRG 523	failure	muthukumar , arunkumar	replaced new	1094574 -1, rel0068 -1,GP005798-1"	due to battery dry	Applied	After grid resume wtg stop due to high break temp | we attend and found brake bad thermistor brake battery backup unit and timer was failure | so replaced new one and wtg started	After change the brake battery power smooth operation done -Field Engineer-Ram Lakshmanan MP | -Field Operations Manager-Ravibala Suresh S.
CIR-10000110	100260947	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-035	0.85	65		ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	21/02/2014		11/03/2016	-0	Ram Lakshmanan MP	1386	1439	11/03/2016 07:35:00	11/03/2016 06:29:00	3441948	17441	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	REL0068		NORMAL OPERATION		Wtg stop due to HW DC link voltage low	Timer	Breakdown	BRG540	Continuos(on and off) operating, Grid Fluctuation.	Ramlakshmanan	timer KR013A changed	1 NO	Continuos(on and off) operating, Grid Fluctuation. Grid down for long time and Fluctuation.	Assigned	Wtg stop due to HW DC link voltage low we attend and found timer KR013A failure.so replace the new one then start the WTG."	Wtg stop due to HW DC link voltage low we attend and found timer KR013A failure.so replace the new one then start the WTG."-Field Engineer-Ram Lakshmanan MP | No Clearance between Timer Relay KR013A and KR913 that's why heat produced and do the malfunction(Failure) in timer-Field Operations Manager-Ravibala Suresh S. | BOP Auditing recommended-Phone Technical Support-Senthil M. | Create DAC tool configuration for this WF-Functionality Support Lead-Murugesan P. | Configuration file to be created for data accusation and further analysis. Meanwhile failed component operating life to be calculated.-Functionality Support Specialist-Mayank | -Quality-Vijay Chinnaswamy	REL0068 Timer.jpg
CIR-10000006	100261437	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-049	2	90.2	LM	ABB type C	4635472	Hansen	EH806A-031/CM0025	Standard+	STD+	Standard	09/04/2015	2345	11/02/2016	420-Gearbox auxiliary pump feedback failure	Perumal P.V	1371	1374	11/02/2016 14:00:45	11/02/2016 12:00:45	43566	234	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	gp124	xvfrt	LIGHTNING	23465	WTG Feedback Problem Motor Failed...	Aux Failure	Rain	Specify	Grid	Per	Change module	12	Temp rise, Oil filter problem	Applied	1. Stop WTG | 2. Check IR Value | 3. Bearing Cond'n | 4. Contactor operation | 5. problem solved	Failure-Field Engineer-Perumal P.V | -Field Operations Manager-Senthilkumar T.
CIR-10000388	100261456	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-001	2	90.2	LM	Cantarey	801251112	Hansen	EH806A-031/CM0030	Standard+	STD+	Standard	11/03/2015	402350246	02/05/2016	208-HU pump activation failure	Anand K.	1459	1460	02/05/2016 05:32:00	02/05/2016 04:15:00	5230519	9358	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP022129	ABB	NORMAL OPERATION		Wtg stopped due to HG feedback failure.We have check and found that KM 280 contactor was failure.	HG cotactor KM 280	Normal operation	Top control panel rear side	Activation failure	A.Sivan perumal	To replaced the KM 280 conatctor	1 no	If we are not replaced the KM280 contactor HG motor pumping time will be increased.	Assigned	We have replaced the KM280 contactor.	We have replaced the Km280 contactor.-Field Engineer-Anand K. | KM280 Contactor replaced.-Field Operations Manager-Perumal P.V | FSL Comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Anand A.P
CIR-10000613	100260947	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-035	0.85	65		ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	21/02/2014	402368017	11/05/2016	411-High brake temperature	Ram Lakshmanan MP	1386	1425	11/05/2016 19:48:35	11/05/2016 17:48:35	3584972	18892	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP005798		NORMAL OPERATION		High brake temperature	brake pad	grid failure	BRG 524	failure	muthu kumar,arun	replaced new brake pad	1		Applied	we are attend and replaced new brake power suppiy unit and brake bad then start tha wtg then start.	we are attend and replaced new brake power suppiy unit then start tha wtg then start.-Field Engineer-Ram Lakshmanan MP | -Field Operations Manager-Ravibala Suresh S.
CIR-10000750	100260948	Mytrah Energy (India) Limited	BURGULA (MYTRAH)	WF-IN-001-1194-Y0-A-037	0.85	65		ABB type C	4622191	Gamesa gearbox	100847	High Temperature	STD+	Standard	21/02/2014	402372299	23/05/2016	-0	Ram Lakshmanan MP	1396	1425	23/05/2016 18:57:52	23/05/2016 16:18:52	3792794	19133	ELECTRICAL	HIGH SPEED SHAFT COUPLING SYSTEM	1094574 -1, rel0068 -1,GP0057		GRID FAILURE		High Brake Temp	brake battery backup unit failure	grid resume	BRG 526	failure	ramlakshmanan, muthupandi	replaced new	1094574 -1, rel0068 -1,GP005798-1"	due to battery dry	Applied	After grid resume wtg stop due to high break temp | we attend and found brake pad thermistor brake battery backup unit and timer was failure | so replaced new one and wtg started	After change the brake battery power smooth operation done -Field Engineer-Ram Lakshmanan MP | -Field Operations Manager-Ravibala Suresh S.
CIR-10000743	100261451	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-046	2	90.2	LM	Cantarey	801251097	Hansen	EH806A-031/CM0019	Standard+	STD+	Standard	02/04/2015		24/06/2016	208-HU pump activation failure	Anand K.	1459	1460	16/06/2016 21:27:00	16/06/2016 19:03:00	5429452	10115	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP022129	ABB	NORMAL OPERATION		KM280 contactor coil was short circuited	KM280 contactor failed	During normal condition	Gamesa Electrical pannel	coils are short circuited	M.Sathish A.Sivanperumal	check the coil continuity of the KM280 contactor and replace it	KM280 contactor-1 No's	HU motor doesn't run	Assigned	we have checked the coil resistance value&continuity | we found coils are short circuited | we replaced the KM280 contactor	KM280 contactor coils are short circuited and we replaced it-Field Engineer-Anand K. | KM280 Contactor replaced-Field Operations Manager-Perumal P.V | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Anand A.P
CIR-10000734	100261556	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-032	2	90.2	LM	Cantarey	801251211	Hansen	EH806A-031/CM0131	Standard+	STD+	Standard	12/03/2015	402383721	06/04/2016	-0	Anand K.	1459	1460	04/06/2016 17:24:00	04/06/2016 08:50:00	5865676	10467	ELECTRICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	GP023338	ABB	NORMAL OPERATION		HG oil temp high.	HG cooling motor	Normal operation	Hg unit	May be loose connection in terminal block	P.V.Perumal, A.Gopalakrishnan,S.Rajashingh.	To replaced the hg cooling motor	1 no	The HG motor pumping count will be more.It will affect the HG main motor's life time.	Assigned	HG oil temp high. We have checked the HG oil temp sensor,RTD module connections,then we have checked the HG oil cooling pump. In that HG oil Cooling pump motor Winding was open. So we have replaced the Motor.	We have checked the main motor terminal connection.-Field Engineer-Anand K. | HG cooling motor replaced-Field Operations Manager-Perumal P.V | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Anand A.P
CIR-10000735	100261468	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-022	2	90.2	LM	Cantarey	801251116	Hansen	EH806A-031/CM0039	Standard+	STD+	Standard	12/03/2015	402383719	04/06/2016	-0	Anand K.	1459	1460	04/06/2016 22:49:00	04/06/2016 02:40:00	5983964	10611	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP091226,GP091145,GP091181,	Ingeteam	NORMAL OPERATION		Double driver card , IGBT assambly .and CCu was failure.	IGBT assambly,Double driver card,CCU	Normal operation	Converter panel	May be grid dip	K.Anand,K.Velmurgan,S.petchinathan,A.Sivan perumal,	To replace the IGBT assambly,Double driver card,CCU	IGBT assambly 6 no's,Double driver card 3 o's,CCU 1 no	It may be affect the Rotor side winding and rotor circuit.	Rejected	We have check and found that IGBT assambly , IGBT double driver card failure in inverter S,R,T . | So we have replaced the all inverter side IGBT assambly and Double driver card. | After that we have check and found that CCU was not working correctely. So we have relaced the CCU also.	We have checked the all inverter side IGBT's terminal connection.-Field Engineer-Anand K. | CCU,Double driver card,IGBT assembly replaced-Field Operations Manager-Perumal P.V | Kindly upload the images &location no in comments-Phone Technical Support-Senthil M. | -Field Engineer-Anand K.
CIR-10000238	100261488	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-014	2	90.2	LM	ABB type C	4635490	Hansen	EH806A-031/CM0070	Standard+	STD+	Standard	12/03/2015	402320345	01/04/2016	-0	Petchi Nathan S.	1422	1435	02/04/2016 03:08:00	01/04/2016 19:56:00	4785463	9073	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	GP037087	PARKER	NORMAL OPERATION		We have checked and found Blade C Accumulator got slipped its original position and it was damaged Accumulator hose and Pitch cylinder drain hose.	Blade C Accumulator Fixing bolt removed from its original position.	During running.	Inside the HUB	Accumulator mounting bolt loosened(check the bolt Torque)	S.Petchinathan,A.Sivanperumal	Replaced Accumulator Hose and Drain hose.	1	Accumulator fixing bolt(Accumulator to HUB frame) got removed from its original position.	Assigned	we have replaced the Accumulator hose and Pitch cylinder drain hose. | We have replaced the Accumulator fixing bolts | We have cleaned the HUB and topped up Hydraulic oil.	Nil-Field Engineer-Petchi Nathan S. | Approved-Field Operations Manager-Perumal P.V | Check nut torque must checked as per the Maintenance check list-Phone Technical Support-Senthil M. | Attached is the field alert to check the torque valves of Accumulator clamps. Please ensure the same in all wtg in the windafrm. As mentioned in 3M & 12M PM checklist, please ensure to check accumulator bolted joints-Functionality Support Lead-Anand A.P | Hi, is the Accumalator bracket moved or the C clampis broken....-Quality-Vijay Chinnaswamy | The C clamps, which has two halfs has broken-Functionality Support Lead-Anand A.P | DM modification available to be implemented-Quality-Vijay Chinnaswamy | Sorry, in this case the Bracket has moved and the bolt were found to be loose, therfore the accumulator has moved and damaged the hydraulic hoses. Please check with plant for torquing of these bolts-Functionality Support Lead-Anand A.P | -Quality-Vijay Chinnaswamy	IMG-20160401-WA0002.jpg | IMG-20160401-WA0003.jpg | IMG-20160401-WA0007.jpg | IMG-20160401-WA0009.jpg | NI8061503 R01 Internal Report for Accumulator bracket bolts loosinging.pdf Attached is the field alert regarding Accumulator clamp torque inspection
CIR-10000744	100261469	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-013	2	90.2	LM	Cantarey	801251127	Hansen	EH806A-031/CM0040	Standard+	STD+	Standard	12/03/2015		20/06/2016	120-Error in Yaw pulses	Anand K.	1459	1460	20/06/2016 08:07:00	20/06/2016 00:38:00	5673279	10772	ELECTRICAL	YAW SYSTEM	GP007686	ABB	NORMAL OPERATION		KM180 contactor was failed due to yaw motor failiure over current	KM180 contactor failed	normal condition	Gamesa Electrical pannel	coils of the contactor are short circuited	A.Sivan perumal	replace the contactor by new one	KM-180 1No's	yaw motor dosn't run	Assigned	we checked the connections | replace the contactor	contactor was replaced and the WTG was running in normal condition-Field Engineer-Anand K. | YAW contactor replaced-Field Operations Manager-Perumal P.V | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.
CIR-10000745	100261469	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-013	2	90.2	LM	Cantarey	801251127	Hansen	EH806A-031/CM0040	Standard+	STD+	Standard	12/03/2015		24/06/2016	-0	Perumal P.V	1459	1460	20/06/2016 08:07:00	20/06/2016 00:38:00	5673279	10772	ELECTRICAL	YAW SYSTEM	GP119762	ABB	NORMAL OPERATION		yaw motor windings are short circuited	yaw motor failed	normal condition	yaw system	short circuit in motor winding	A.Sivanperumal M.Sathish	replace motor by new one	1-No's	yaw system doesn't works	Rejected	we check the motor connections | replaced the motor	yaw motor was replaced, now the WTG was running in normal condition-Field Engineer-Anand K. | YAW motor replaced-Field Operations Manager-Perumal P.V | Kindly update the images-Phone Technical Support-Senthil M. | -Field Engineer-Anand K.
CIR-10000387	100261466	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-024	2	90.2	LM	Cantarey	801251117	Hansen	EH806A-031/CM0035	Standard+	STD+	Standard	12/03/2015	402348064	14/05/2016	208-HU pump activation failure	Anand K.	1459	1460	28/04/2016 13:58:00	29/04/2016 12:18:00	5298107	9718	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP022129	ABB	NORMAL OPERATION		Wtg stopped due to HG feedback failure.We have check and found that KM280 contactor was failure.	HG contactor KM280	Normal operation	Top control panel rear side	KM280 contactor activation failure	A.Sivan perumal	To replace the KM280 contactor.	1 no	If we are not replaced the contactor the error cames repectly.	Rejected	We have replaced the KM280 contactor	We have replaced the KM280 contactor.-Field Engineer-Anand K. | KM280 Contactor replaced.-Field Operations Manager-Perumal P.V | Query repeated-Phone Technical Support-Senthil M. | -Field Engineer-Anand K.
CIR-10000385	100261464	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-020	2	90.2	LM	Cantarey	801251128	Hansen	EH806A-031/CM0038	Standard+	STD+	Standard	14/03/2015	402332756	13/04/2016	-0	Anand K.	1459	1435	13/04/2016 05:10:00	13/04/2016 15:25:00	5153590	9143	CONTROL SYSTEM	NACELLE INSTRUMENTATION SYSTEM	GP189308		NORMAL OPERATION		Wtg stopped due to High (Atmospheric ) T.We have check and found that sonic sensor was failure.	Ultra sonic sensor.	Normal operation	Nacelle top	Mal function of Ultra sonic sensor	K.Anand, A.Sivan perumal	To replaced the Ultra sonic sensor.	1 no	If we are not replaced the sensor the air temp wt as showing correctly .Because of this if the temp above 40 degree the wtg goes from run mode to pause mode. we unable to get run the wtg.	Assigned	We have replaced the new sonic sensor .	In this wtg before replaced the sonic sensor the temp valve was 4 degree more then the nearest wtg.-Field Engineer-Anand K. | Ultra sonic sensor replaced-Field Operations Manager-Perumal P.V | FSL Comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Shankar Anand R.
CIR-10000733	100261469	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-013	2	90.2	LM	Cantarey	801251127	Hansen	EH806A-031/CM0040	Standard+	STD+	Standard	12/03/2015	402379524	31/05/2016	-0	Perumal P.V	1459	1460	30/05/2016 14:48:00	29/05/2016 18:29:00	5234569	10276	ELECTRICAL	ELECTRICAL CABINET SYSTEM	gp235458,gp235479	ABB	NORMAL OPERATION		ACB closing coil failed so replaced the new ACB coil	ACB Closing and opening coil	Normal operation	Top Converter panel	During grid drop	K.Anand, A.Goplakrishan,S.Petchinathan	To replace the ACB coil	3	May be that ACB got fail.	Assigned	1.Converter panel door limit switch circuit checked. 2.KR 001,KR003,KR900 relay working conditions checked. 3.ACB closing coil, Opening coil and Voltage minmum coil cable connections checked.	We have checked all the ACB feedback cables in terminal block and CCU-Field Engineer-Anand K. | ACB closing coil replaced-Field Operations Manager-Perumal P.V | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.
CIR-10000380	100261458	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-018	2	90.2	LM	Cantarey	801251115	Hansen	EH806A-031/CM0027	Standard+	STD+	Standard	11/03/2015	402326000	05/04/2016	-0	Petchi Nathan S.	1459	0	05/04/2016 15:46:00	05/04/2016 12:51:00	4726562	9215	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP132911		NORMAL OPERATION		We have checked the related connections found Lambda power supply got failure.	F.A. POWER SUPPLY LAMBDA	During running	Ingeeteam Cabinet control supply		K.Anand,A.Sivanperumal	Replaced the Power supply	1	Due to ambient temperature electronics component got failed.	Assigned	Power supply incoming supply checked found normal. | Power supply output voltage was in low.	PLC converter communication error for approval-Field Engineer-Petchi Nathan S. | Lambda power supply replaced-Field Operations Manager-Perumal P.V | FSL Comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.
CIR-10000736	100261463	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-003	2	90.2	LM	Cantarey	801251118	Hansen	EH806A-031/CM0033	Standard+	STD+	Standard	14/03/2015	402391470	12/06/2016	208-HU pump activation failure	Anand K.	1459	1460	12/06/2016 13:44:00	12/06/2016 12:19:00	5972547	10527	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP022129	ABB	NORMAL OPERATION		We have checked and found HG motor contactor KM280 failure. We have replacde with new one.	HG motor Contactor	Normal operation	HG unit Contactor	Contactor's continous operation	A.Gopalakrishnan, A.Sivan perumal	To replaced the new contactor	1 no	If it's continous HG main pump motor may be failure.	Assigned	1.We have checked MPCB connection. | 2.We have checked HG motor winding. | 3.We have checked and found HG contactor failure. So we have replaced with new one.	We have checked the HG unit contactor's terminal connections.-Field Engineer-Anand K. | KM280 contactor replaced-Field Operations Manager-Perumal P.V | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Anand A.P
CIR-10000392	100261455	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-002	2	90.2	LM	Cantarey	801251099	Hansen	EH806A-031/CM0024	Standard+	STD+	Standard	11/03/2015		14/05/2016	208-HU pump activation failure	Anand K.	1459	1460	11/05/2016 13:01:00	11/05/2016 10:51:00	5261681	9837	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP022129	ABB	NORMAL OPERATION		Wtg stopped due to HG feedback failure.We have check and found that KM280 contactor was failure.	HG contactor KM280	Normal operation	Top control panel rear side	Activation failure	K.Anand	To replace the new Contactor	1 no	If we are not replaced the KM280 contactor Pumping time of the HG pump will be very high.It will increase the HG oil temp.	Assigned	We have replaced the KM 280 contactor .	We have replaced the KM280 contactor.-Field Engineer-Anand K. | KM280 Contactor replaced-Field Operations Manager-Perumal P.V | FSL Comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Anand A.P
CIR-10000384	100261490	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-026	2	90.2	LM	ABB type C	4638232	Hansen	EH806A-031/CM0075	Standard+	STD+	Standard	11/03/2015	402327311	09/04/2016	-0	Anand K.	1371	1373	09/04/2016 18:59:00	09/04/2016 03:11:00	5077713	9393	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	GP118568	VICKERS	NORMAL OPERATION		Wtg stopped due to Pitch activation failure.We have check and found that Propositional valve was failure.	Propositional valve	Normal operation	Blade C	Activation failure.	A.Gopala krishnan	To replace the valve by new one	1 no	If we are not replaced the valve the error was not reset.	Assigned	We have replaced the new Propositional valve.	We have replaced the valve and run the wtg.-Field Engineer-Anand K. | Proportional valve replaced.-Field Operations Manager-Perumal P.V | FSL Comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Anand A.P
CIR-10000391	100261450	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-008	2	90.2	LM	ABB type C	4635468	Hansen	EH806A-031/CM0020	Standard+	STD+	Standard	13/03/2015	402354474	06/05/2016	-0	Anand K.	1459	1460	06/05/2016 21:38:00	06/05/2016 18:44:00	5422482	9896	ELECTRICAL	GEARBOX SYSTEM	GP097229	ABB	NORMAL OPERATION		Wtg stopped due to Gear box oil temp high.We have check and found that Gear box motor was failure.	Gear oil pump with motor	Normal operation	Nacelle	Activation failure	P.V.Perumal, Rajasingh	To replace the Gear oil pump	1 no	If we are not replaced the pump the gear box oil temp error was continuously occured.	Assigned	We have replaced the Gear box Motor with pump.	We have replaced the Gear oil motor with pump-Field Engineer-Anand K. | Gearbox main pump motor replaced-Field Operations Manager-Perumal P.V | FSL Comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Anand A.P
CIR-10000741	100261458	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-018	2	90.2	LM	Cantarey	801251115	Hansen	EH806A-031/CM0027	Standard+	STD+	Standard	11/03/2015	402399638	16/06/2016	-0	Perumal P.V	1459	1460	17/06/2016 15:33:00	16/06/2016 08:44:00	5626663	16810	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP091030	ABB	NORMAL OPERATION		KM052R rotor protection contactor failure.	KM052R contactor failure.	During normal operation.	Converter panel	Lose connection	P.V.Perumal,T.Arulprakash,S.Petchinathan,A.Sivanperumal,NGopalakrishnan,Udhayakumar, Jenish	Replaced new one KM052R contactor.	260A contactor-1no	KM052R contactor shortcircuit problem.	Assigned	We have checked cable connection and contactor continuity. | KM052R contactor machanicham failure. | So replaced with new one.	KM052R contactor failed. So replaced new one.-Field Engineer-Anand K. | KM052R Contactor replaced-Field Operations Manager-Perumal P.V | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.
CIR-10000742	100261458	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-018	2	90.2	LM	Cantarey	801251115	Hansen	EH806A-031/CM0027	Standard+	STD+	Standard	11/03/2015	402399638	16/06/2016	-0	Anand K.	1459	1460	17/06/2016 15:33:00	16/06/2016 08:44:00	5626663	10810	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP040689	ABB	NORMAL OPERATION		contactor was failed due to short circuit	KC 002 conductor was failed	during WTG normal running condition	In Ingeteam converter pannel	coil short circuit	P.V.Perumal T.Arul prakash N.Gopalakrishnan S.Petchinathan udhayakumar genis sivanperumal	repaced by new one	KC002 contactor 1'Nos	it will burn the r phase IGBT card	Rejected	we have checked the coil resistance value and continiuty | we found that the coil was short circuited | then we replaced it	KC 002 contactor Connections are checked-Field Engineer-Anand K. | Confirm material-Field Operations Manager-Perumal P.V | -Field Engineer-Anand K.
CIR-10000253	100261481	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-010	2	90.2	LM	ABB type C	4635487	Hansen	EH806A-031/CM0048	Standard+	STD+	Standard	12/03/2015		08/04/2016	-0	Petchi Nathan S.	1422	1435	08/04/2016 13:12:00	08/04/2016 06:50:00	4975062	9145	ELECTRICAL	YAW SYSTEM	GP119762	ABB	NORMAL OPERATION		Yaw motor 2 got failure(U1 U2 winding got opened).	Yaw motor	During Yawing	ETP2 41 Nacelle	Frequent operation in low wind	S.Petchinathan,A.Sivanperumal	New Yaw motor replaced	1	Frequent operation in low wind	Assigned	We have checked the related connections and all yaw motor winding resistance value. | We found Yaw motor 2 U1-U2 winding got opened. | We have replaced the yaw motor by new one.	Yaw motor replaced-Field Engineer-Petchi Nathan S. | Approved-Field Operations Manager-Perumal P.V | Closed-Phone Technical Support-Senthil M. | closed-Functionality Support Lead-Murugesan P. | -Quality-Vijay Chinnaswamy	IMG_20160408_133531.jpg | IMG_20160408_133516.jpg
CIR-10000383	100261481	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-010	2	90.2	LM	ABB type C	4635487	Hansen	EH806A-031/CM0048	Standard+	STD+	Standard	12/03/2015	402327099	14/05/2016	-0	Anand K.	1371	0	08/04/2016 12:12:00	08/04/2016 06:50:00	4975062	9280	ELECTRICAL	YAW SYSTEM	GP119762	ABB	NORMAL OPERATION		Wtg stopped due to Yaw motor over current.We have check and found that 181B yaw motor winding was open.	Yaw motor	Normal operation	Nacelle control panel side yaw motor	Winding was open	S.Petchinathan, A.Sivan perumal	To replace the new Yaw motor	1 no	If we are not replaced the motor the other 3 motor's got over load and may be chance of failure.	Assigned	Yaw motor winding was open so we have replaced the new yaw motor.	We have replaced the yaw motor and we have checked other 3 motor's winding connections and tightness.-Field Engineer-Anand K. | YAW motor replaced-Field Operations Manager-Perumal P.V | FSL Comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.
CIR-10000386	100261481	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-010	2	90.2	LM	ABB type C	4635487	Hansen	EH806A-031/CM0048	Standard+	STD+	Standard	12/03/2015	402347379	14/05/2016	208-HU pump activation failure	Anand K.	1459	1460	28/04/2016 22:35:00	28/04/2016 15:15:00	5101376	9650	ELECTRICAL	YAW SYSTEM	GP119762	ABB	NORMAL OPERATION		Wtg stopped due to Yaw motor over current .We have check and found that Yaw motor was failure.	Yaw motor	Normal operation	Nacelle coupling side	winding open	P.V.Perumal	To replaced the new yaw motor	1 no		Rejected	We have replaced the new yaw motor.	We have replaced the yaw motor .-Field Engineer-Anand K. | Yaw motor replaced.-Field Operations Manager-Perumal P.V | Query repeated-Phone Technical Support-Senthil M. | -Field Engineer-Anand K.
CIR-10000731	100261481	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-010	2	90.2	LM	ABB type C	4635487	Hansen	EH806A-031/CM0048	Standard+	STD+	Standard	12/03/2015		13/05/2016	205-Low oil level in hydraulic unit	Anand K.	1459	1460	13/05/2016 17:36:00	13/05/2016 10:37:00	5214747	9948	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL		Trelle Borg	NORMAL OPERATION		Wtg stopped due to HG oil level low .We have check and found that A blade Pich cylinder oil seal was failure.	A blade pitch cylinder's oil seal failure	Normal operation	Hub A blade pitch cylinder	HG oil leakage	Suresh,Petchinathan,Elango	To replace the pitch cylinder's oil seal .	8 set	If we are not changr the oil seal in the A blade pitch cylinder HG oil leakage was happen .It will create the HG oil level low alarm and every time we have to top up the HG oil.	Assigned	We have replaced the A blade pitch cylinder's oil seal 8 sets. | The material part no's are GR6900900-C380,WEYE19099T40N , ORAR00354-N70 , GR7400900-C380 , ORAR00157-N70 , RSV300900-T19N , BBP80B354-N962N , RSYE042695T19N ,	we have replaced the A blade pitch cylinder's oil seal .-Field Engineer-Anand K. | Pitch cylinder oil seal replaced-Field Operations Manager-Perumal P.V | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Anand A.P
CIR-10000334	100260000	Gamesa Wind Turbines Pvt. Ltd	PATTAN	WF-IN-006-1144-Y0-A-006	0.8	65	Standard	ABB type C	CVVV12334234	Hansen	CVVV12334234	High Temperature	STD+	Standard	18/08/2012			329-Tower Door fan failure	Administrator	0	0	01/01/1900 00:00:00	01/01/1900 00:00:00	0	0	MECHANICAL	TOWER SYSTEM			NORMAL OPERATION		test entry to check the tower issue										Fix tower door | repair tower door
CIR-10000335	100260000	Gamesa Wind Turbines Pvt. Ltd	PATTAN	WF-IN-006-1144-Y0-A-006	0.8	65	Standard	ABB type C	CVVV12334234	Hansen	CVVV12334234	High Temperature	STD+	Standard	18/08/2012			329-Tower Door fan failure	Manoj D.	0	0	01/01/1900 00:00:00	01/01/1900 00:00:00	0	0	MECHANICAL	TOWER SYSTEM			NORMAL OPERATION		test entry for the tower issue									Applied	repair tower	assign to FOM by FE-Field Engineer-Manoj D. | -Field Operations Manager-Chirag R Patel
CIR-10000696	100260814	New & Renewable Energy Development Corporation of Andhra Pradesh Ltd.	REKULAKUNTA	WF-IN-001-1134-Y0-A-006	0.85	65		ABB type C	4605484	Hansen	EH806A-001-LM0001	High Temperature	STD+	Standard	29/03/2012		16/06/2016	3232-Synchronization timeout	Seenivasagan G.	1404	1425	16/06/2016 03:22:00	12/06/2016 21:10:00	7370129	32612	ELECTRICAL	GENERATOR SYSTEM			NORMAL OPERATION		Generator rpm counter is mismatched encoder coupler failure	Generator encoder coupler problem	Normal running	Generator system	Coupler loose connection		replaced new encoder coupler	1Nos replaced	It will created generator synchronizes problem		While inspection generator coupler was failure after replaced new coupler
CIR-10000737	100261458	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-018	2	90.2	LM	Cantarey	801251115	Hansen	EH806A-031/CM0027	Standard+	STD+	Standard	11/03/2015	402399635	14/06/2016	-0	Perumal P.V	1459	1460	14/06/2016 20:32:00	14/06/2016 14:48:00	5580366	10784	CONTROL SYSTEM	HYDRAULIC SYSTEM AND PITCH CONTROL	GP122842	ABB	NORMAL OPERATION		Grid voltage failure due to HG main pump motor was failure.	HG motor	Normal operation	HG unit	winding insulation failure	P.V.Perumal,S.Pechtinathan,M.Satish,A.Gopalakrishnan.	To replace the HG motor	1 no		Assigned	1. We have checked the all motor's connections. | 2.Then we reset the wtg .That time FG280 Mccb was tripped. So we have checked the MCCB , Contactor and HG pump motor. | 3. Then we have checked the HG motor ,in that we have check and found that Motor winding U and V was short circuited. | 4.So we have replaced the HG main pump motor.	We have replaced the HG motor and we have checked all motor's terminal connections.-Field Engineer-Anand K. | Hydraulic motor replaced-Field Operations Manager-Perumal P.V | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Anand A.P
CIR-10000738	100261458	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-018	2	90.2	LM	Cantarey	801251115	Hansen	EH806A-031/CM0027	Standard+	STD+	Standard	11/03/2015	402399638	23/06/2016	-0	Perumal P.V	1459	1460	17/06/2016 15:33:00	16/06/2016 08:44:00	5626663	10810	ELECTRICAL	ELECTRICAL CABINET SYSTEM	gp119052,gp023867,gp091016		NORMAL OPERATION		Magnetothermic trigger of the line protection due to 125A fuse failure.	125A fuse, 2.7uf capacitor, 1K ohm resister	Normal operation	Converter	May be over voltage	P.V.Perumal,T.Arulprakash, S.Petchinathan,N.Gopalakrishnan,A.Sivanperumal,Uathayakumar,Jenis.	To be replaced the 125A fuse,2.7uf capacitor,1K ohm resister.	125A fuse - 4nos 2.7uf capacitor - 3nos 1K ohm resister - 5nos		Rejected	1.We have checked 125A fuse, 2.7uf capacitor and 1K ohm resister failure. | 2.So we replaced the 125A fuse, 2.7uf capacitor, 1K ohm resister.	We have checked that 125A fuse, cable connections-Field Engineer-Anand K. | 125A HRC fuse replaced-Field Operations Manager-Perumal P.V | Kindly update the failure parts images-Phone Technical Support-Senthil M. | -Field Engineer-Anand K.
CIR-10000739	100261458	ENERGON POWER RESOURCES PRIVATE LTD	TAGGUPARTHI-G9X (ENERGON-II)	WF-IN-001-1315-Y0-A-018	2	90.2	LM	Cantarey	801251115	Hansen	EH806A-031/CM0027	Standard+	STD+	Standard	11/03/2015	402399638	16/06/2016	-0	Perumal P.V	1459	1460	24/06/2016 10:03:00	16/06/2016 10:03:00	5626663	10810	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	gp091027	ABB	NORMAL OPERATION		Due to Magneto thermic trigger of the line protection error FG005 MCCB got failed.	FG005 breaker failure	During normal operation	Ingeteam power panel	Single phasing	P.V.Perumal,T.Arulprakash, S.Petchinathan,A.Sivanperumal,N.Gopalakrishnan,Udhayakumar,Jenis	Replace the FG005 breaker	320A breaker-1no	SF6 breaker may have tripped.	Assigned	We have check and found that FG005 MCCB was failure. | So we have replaced with the new one.	FG005 breaker all connection tightness to be checked.-Field Engineer-Anand K. | FG005 MCCB replaced-Field Operations Manager-Perumal P.V | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.
CIR-10000532	100260175	EVEREADY SPINNING MILLS (P) LIMITED	ELAVANTHI	WF-IN-022-0884-Y1-A-001	0.85	65	Standard	Indar	20305001236	Gamesa(China)	602148	High Temperature	STD+	Standard	30/09/2010	402346998	28/04/2016	-0	Yathavaraj V	1404	1437	28/04/2016 23:00:00	28/04/2016 21:00:45	8916010	42184	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP004888	PHONIX CONTACT	NORMAL OPERATION	1113687379	2118.BUS ERROR INTER BUS FAILURE	CAB MODULE FAILURE	NORNAL OPERATION TIME	TOP CONTROL PANEL	MODULE COMPRESSING OR MODULE FAILURE	TOP MODULE COMMUNICATION	DURING NORMAL OPERATION TIME MODULE HAD FAILED	01 NUMBER	WTG STOPPED DUE TO ERROR 2118.BUS ERROR INTER BUS FAILURE. WE HAD CHECKED THE DISPLAY ERROR LOG FOUND THAT THE ERROR CODE IS 3.0. AND TOO FURTHER CHECKING FOUND THAT CAB MODULE WAS FAILED CONDITION. SO WE REPLACED THE MODULE WITH NEW ONE. THERE AFTER RESTART THE WTG	Assigned	WTG STOPPED DUE TO ERROR 2118.BUS ERROR INTER BUS FAILURE. WE HAD CHECKED THE DISPLAY ERROR LOG FOUND THAT THE ERROR CODE IS 3.0. AND TOO FURTHER CHECKING FOUND THAT CAB MODULE WAS FAILED CONDITION. SO WE REPLACED THE MODULE WITH NEW ONE. THERE AFTER RESTART THE WTG	WTG STOPPED DUE TO ERROR 2118.BUS ERROR INTER BUS FAILURE. WE HAD CHECKED THE DISPLAY ERROR LOG FOUND THAT THE ERROR CODE IS 3.0. AND TOO FURTHER CHECKING FOUND THAT CAB MODULE WAS FAILED CONDITION. SO WE REPLACED THE MODULE WITH NEW ONE. THERE AFTER RESTART THE WTG -Field Engineer-Yathavaraj V | SF.NO:- 244 EVEREADY 2 WTG TOP CONTRO PANEL CAB MODULE FAILURE-Field Operations Manager-Dhanabal S | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.
CIR-10000222	100260085	BMM Paper Board (P) Ltd	Theni-Kadamalaigundu	WF-IN-022-0846-Y2-A-008	0.85	65	Standard	Indar	20305001108	Gamesa(China)	601957	High Temperature	STD+	Standard	19/05/2010	402319479	28/03/2016	-0	Devasudar Singh	1404	1440	28/03/2016 14:45:00	28/03/2016 11:00:00	7851100	41930	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP012585,GP012532,GP012531,GP188019,50074,50071	INGETEAM, SAFETEC,ABB,EUPEC	NORMAL OPERATION	2263112547,116068170,56465005686,69721392
CIR-10000245	100260085	BMM Paper Board (P) Ltd	Theni-Kadamalaigundu	WF-IN-022-0846-Y2-A-008	0.85	65	Standard	Indar	20305001108	Gamesa(China)	601957	High Temperature	STD+	Standard	19/05/2010	121	06/04/2016	111-Max hydraulic unit pumping time	Jeno V	1372	1425	06/04/2016 16:44:41	06/04/2016 16:44:41	21212	12	CONTROL SYSTEM	BUILT-IN SYSTEMS	1212	1212	GRID FAILURE	1221	Test for data sync								Test for data sync	Deleted	Test for data sync
CIR-10000246	100260085	BMM Paper Board (P) Ltd	Theni-Kadamalaigundu	WF-IN-022-0846-Y2-A-008	0.85	65	Standard	Indar	20305001108	Gamesa(China)	601957	High Temperature	STD+	Standard	19/05/2010	22	06/04/2016	113-Yaw motors thermomagnetic relay failure	Jeno V	1372	1374	06/04/2016 16:55:36	06/04/2016 16:55:36	111	11	CONTROL SYSTEM	BLADE BEARING SYSTEM	11	11	GRID FAILURE	111	ASDASD									Deleted	ASD
CIR-10000340	100260176	ARKAY ENERGY (RAMESWARAM) LIMITED	Theni-Kadamalaigundu	WF-IN-022-0872-Y2-A-004	0.85	65	Standard	Indar	20305001238	Gamesa(China)	602170	High Temperature	STD+	Standard	29/03/2011	402350099	01/05/2016	-0	Devasudar Singh	1404	1440	01/05/2016 08:15:00	01/05/2016 06:00:00	8058720	36763	ELECTRICAL	ELECTRICAL CABINET SYSTEM	50103	EMC	NORMAL OPERATION		Wtg stopped due to error no:2242 FG5 failure . so we check & found Current filter was failure.	EMC filter was failure	Breakdown	SF.NO:501(JATTIN)	Continuous operation	S.Johnpeter, G.Bala	EMC filter replaced by new one	01no	Continuous operation, grid drop	Assigned	we replaced filter by new one.	Wtg stopped due to error no:2242 FG5 failure . so we check & found Current filter was failure.we replaced by new one.-Field Engineer-Balasubramanian G. | Problem solved-Field Operations Manager-Devasudar Singh | BOP Auditing recommended-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.	IMG_20160502_114311.jpg EMC Filter
CIR-10000265	100260161	CHERAN SPINNER LIMITED	Theni-Kadamalaigundu	WF-IN-022-0872-Y2-A-003	0.85	65	Standard	Indar	20305001208	Gamesa(Spain)	300034	High Temperature	STD+	Standard	28/09/2010	402328198	09/04/2016	-0	Devasudar Singh	1404	1440	09/04/2016 17:00:00	09/04/2016 16:30:00	8074370	39832	ELECTRICAL	NACELLE INSTRUMENTATION SYSTEM	P393462	ABB	NORMAL OPERATION		During service time error no:206 Hu.protection tripped, we check &found KM280 contactor failure,	KM280 contactor failure	During service time	SF.NO:412(Cheran)	Continuous operation	D.Yukesh, G.Senthilkannan, T.Stalinkumar	we replaced new KM280 contactor	01no	Continuous operation	Assigned	So we changed New KM280 contactor	During service time error no:206 Hu.protection tripped, we check &found KM280 contactor failure,so we replaced by new contactor & restart the turbine.-Field Engineer-Senthil Kannan G | Problem solved-Field Operations Manager-Devasudar Singh	IMG_20160202_164656_HDR.jpg KM280
CIR-10000280	100260162	CHERAN SPINNER LIMITED	Theni-Kadamalaigundu	WF-IN-022-0872-Y2-A-001	0.85	65	Standard	Indar	20305001201	Gamesa(China)	602120	High Temperature	STD+	Standard	28/09/2010	402330324	12/04/2016	-0	Devasudar Singh	1404	1440	12/04/2016 16:30:00	12/04/2016 15:30:00	7784380	39812	ELECTRICAL	NACELLE INSTRUMENTATION SYSTEM	P393462	ABB	NORMAL OPERATION		During service time error no:206 Hu.Activation failure.so we check & found KM 280 contactor failure.	KM280 CONTACTOR FAILURE	During service time	SF.NO:375(Cheran)	Continuous operation, grid drop	R.Dineshbabu, G.Senthilkannan, K.Sankaranarayanan	KM280 contactor replaced by new one.	01no	continuous operation, grid drop	Assigned	We replaced Km280 contactor by new one.	During service time error no:206 Hu.Activation failure.so we check & found KM 280 contactor failure.So we replaced by new one, now machine running normal.-Field Engineer-Dinesh Babu R. | Problem solved-Field Operations Manager-Devasudar Singh	IMG_20160202_164656_HDR.jpg KM280 contactor
CIR-10000556	100260213	Plant Lipids (P) Ltd	ELAVANTHI	WF-IN-022-0833-Y1-A-010	0.85	65	Standard	Indar	20305001233	Gamesa(Spain)	300056	High Temperature	STD+	Standard	27/01/2011	402361786	11/05/2016	-0	Pradhaban N.	1404	1437	11/05/2016 17:30:00	11/05/2016 15:30:00	6727750	40052	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP004892	PHONIX CONTACT	NORMAL OPERATION	1115800997	2118.BUS ERROR INTER BUS FAILURE & 411.HIGH BRAKE ON TEMPERATURE	MODULE FAILURE	WTG DURING NORMAL OPERATION.	TOP CONTROL PANEL	MODULE FAILURE OR VOLTAGE PROBLEM	D/I MODULE	MODULE FAILURE	01 NUMBER	WTG STOPPED DUE TO ERROR 2118.BUS ERROR INTER BUS FAILURE. WE CHECKED THE BUS FAILURE LOG, FOUND THAT THE ERROR CODE DEFINED AS A ED6 MODULE FAILURE AND TOO BRAKE PAD WITH THERMISTOR OPENED IN CONDITION. SO WE REPLACED THE ED6 MODULE AND BRAKE PAD WITH THERMISTOR BY NEW ONE. THERE AFTER WTG PUT BACK INTO OPERATION MODE.	Assigned	WTG STOPPED DUE TO ERROR 2118.BUS ERROR INTER BUS FAILURE. WE CHECKED THE BUS FAILURE LOG, FOUND THAT THE ERROR CODE DEFINED AS A ED6 MODULE FAILURE AND TOO BRAKE PAD WITH THERMISTOR OPENED IN CONDITION. SO WE REPLACED THE ED6 MODULE AND BRAKE PAD WITH THERMISTOR BY NEW ONE. THERE AFTER WTG PUT BACK	WTG STOPPED DUE TO ERROR 2118.BUS ERROR INTER BUS FAILURE. WE CHECKED THE BUS FAILURE LOG, FOUND THAT THE ERROR CODE DEFINED AS A ED6 MODULE FAILURE AND TOO BRAKE PAD WITH THERMISTOR OPENED IN CONDITION. SO WE REPLACED THE ED6 MODULE AND BRAKE PAD WITH THERMISTOR BY NEW ONE. THERE AFTER WTG PUT BACK INTO OPERATION MODE. -Field Engineer-Pradhaban N. | SF.NO:-71/2 SUPERSALES 02 WTG 230V/5AMPS POWER SUPLY UNIT FAILURE-Field Operations Manager-Dhanabal S | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Shankar Anand R.	SF.NO 216 IMG_20160526_164418.jpg
CIR-10000524	100260077	Sri Velayudhaswamy Spinning Mills (P) Ltd.	ELAVANTHI	WF-IN-022-0833-Y1-A-016	0.85	65	Standard	Indar	20305001120	Gamesa(China)	601928	High Temperature	STD+	Standard	13/05/2010	402334870	18/04/2016	-0	Mylsamy P.	1373	1437	18/04/2016 14:45:00	18/04/2016 13:45:00	8138990	45283	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP012585	INGETEAM	GRID FAILURE	AK9670*69714189	WTG STOPPED DUE TO ERROR 700 -PLC. CONVERTOR COMM.FAIL. ON CHECKING THE ERROR, FOUND THAT CCU WAS IN ERROR MODE, THE ERROR CODE IS H1 AND CCU NOT CONNECTED TO LAPTOP, SO WE RESET THE CCU BY PRESSING OF RESET BUTTON IN CCU AND THEN RE-PROGRAM THE CCU FOUND OK THEN RESET THE WTG, DURING THAT TIME AGAIN CCU GOES TO ERROR MODE. HENCE FORTH WE CONFIRMED CCU WAS FAILURE. SO REPLACED THE CCU BY NEW ONE. THEN UPLOAD THE FIRMWARE AND CHECKED ERROR FREE FOUND OK. THERE AFTER WTG PUT BACK INTO OPERATION MO	DFM CCU FAILURE	AFTER GRID FAILURE	BOTTOM CONTROL PANEL	GRID FLUXUATION	INGETEAM CCU	AFTER GRID FAILURE	01 NUMBER	WTG STOPPED DUE TO ERROR 700 -PLC. CONVERTOR COMM.FAIL. ON CHECKING THE ERROR, FOUND THAT CCU WAS IN ERROR MODE, THE ERROR CODE IS H1 AND CCU NOT CONNECTED TO LAPTOP, SO WE RESET THE CCU BY PRESSING OF RESET BUTTON IN CCU AND THEN RE-PROGRAM THE CCU FOUND OK THEN RESET THE WTG, DURING THAT TIME AGAIN CCU GOES TO ERROR MODE. HENCE FORTH WE CONFIRMED CCU WAS FAILURE. SO REPLACED THE CCU BY NEW ONE. THEN UPLOAD THE FIRMWARE AND CHECKED ERROR FREE FOUND OK. THERE AFTER WTG PUT BACK INTO OPERATION MO		ON CHECKING THE ERROR, FOUND THAT CCU WAS IN ERROR MODE, THE ERROR CODE IS H1 AND CCU NOT CONNECTED TO LAPTOP, SO WE RESET THE CCU BY PRESSING OF RESET BUTTON IN CCU AND THEN RE-PROGRAM THE CCU FOUND OK THEN RESET THE WTG, DURING THAT TIME AGAIN CCU GOES TO ERROR MODE. HENCE FORTH WE CONFIRMED CCU W
CIR-10000525	100260077	Sri Velayudhaswamy Spinning Mills (P) Ltd.	ELAVANTHI	WF-IN-022-0833-Y1-A-016	0.85	65	Standard	Indar	20305001120	Gamesa(China)	601928	High Temperature	STD+	Standard	13/05/2010	402334870	04/08/2016	-0	Mylsamy P.	1394	1437	04/08/2016 14:45:00	04/08/2016 13:45:00	8138990	45283	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP012585	INGETEAM	GRID FAILURE	AK9670*69724189	WTG STOPPED DUE TO ERROR 700 -PLC. CONVERTOR COMM.FAIL. ON CHECKING THE ERROR, FOUND THAT CCU WAS IN ERROR MODE, THE ERROR CODE IS H1 AND CCU NOT CONNECTED TO LAPTOP, SO WE RESET THE CCU BY PRESSING OF RESET BUTTON IN CCU AND THEN RE-PROGRAM THE CCU FOUND OK THEN RESET THE WTG, DURING THAT TIME AGAIN CCU GOES TO ERROR MODE. HENCE FORTH WE CONFIRMED CCU WAS FAILURE.	CCU FAILURE	AFTER GRID FAILURE	BOTTOM CONTRO PANEL	GRID FLXUATION	CONVERTER CONTROL UNIT	AFTER GRID FAILURE	01 NUMBER	WTG STOPPED DUE TO ERROR 700 -PLC. CONVERTOR COMM.FAIL. ON CHECKING THE ERROR, FOUND THAT CCU WAS IN ERROR MODE, THE ERROR CODE IS H1 AND CCU NOT CONNECTED TO LAPTOP, SO WE RESET THE CCU BY PRESSING OF RESET BUTTON IN CCU AND THEN RE-PROGRAM THE CCU FOUND OK THEN RESET THE WTG, DURING THAT TIME AGAIN CCU GOES TO ERROR MODE. HENCE FORTH WE CONFIRMED CCU WAS FAILURE. SO REPLACED THE CCU BY NEW ONE. THEN UPLOAD THE FIRMWARE AND CHECKED ERROR FREE FOUND OK. THERE AFTER WTG PUT BACK INTO OPERATION MODE.	Rejected	WTG STOPPED DUE TO ERROR 700 -PLC. CONVERTOR COMM.FAIL. ON CHECKING THE ERROR, FOUND THAT CCU WAS IN ERROR MODE, THE ERROR CODE IS H1 AND CCU NOT CONNECTED TO LAPTOP, SO WE RESET THE CCU BY PRESSING OF RESET BUTTON IN CCU AND THEN RE-PROGRAM THE CCU FOUND OK THEN RESET THE WTG, DURING THAT TIME AGAIN CCU GOES TO ERROR MODE. HENCE FORTH WE CONFIRMED CCU WAS FAILURE. SO REPLACED THE CCU BY NEW ONE. THEN UPLOAD THE FIRMWARE AND CHECKED ERROR FREE FOUND OK. THERE AFTER WTG PUT BACK INTO OPERATION MO	WTG STOPPED DUE TO ERROR 700 -PLC. CONVERTOR COMM.FAIL. ON CHECKING THE ERROR, FOUND THAT CCU WAS IN ERROR MODE, THE ERROR CODE IS H1 AND CCU NOT CONNECTED TO LAPTOP, SO WE RESET THE CCU BY PRESSING OF RESET BUTTON IN CCU AND THEN RE-PROGRAM THE CCU FOUND OK THEN RESET THE WTG, DURING THAT TIME AGAIN CCU GOES TO ERROR MODE. HENCE FORTH WE CONFIRMED CCU WAS FAILURE. SO REPLACED THE CCU BY NEW ONE. THEN UPLOAD THE FIRMWARE AND CHECKED ERROR FREE FOUND OK. THERE AFTER WTG PUT BACK INTO OPERATION MO-Field Engineer-Mylsamy P. | SF.NO:- 265 SVSM4 WTG DFM CCU FAILURE-Field Operations Manager-Dhanabal S | Query repeated-Phone Technical Support-Senthil M. | -Field Engineer-Mylsamy P.
CIR-10000530	100260077	Sri Velayudhaswamy Spinning Mills (P) Ltd.	ELAVANTHI	WF-IN-022-0833-Y1-A-016	0.85	65	Standard	Indar	20305001120	Gamesa(China)	601928	High Temperature	STD+	Standard	13/05/2010	402334870	18/04/2016	-0	Mylsamy P.	1373	1437	18/04/2016 14:45:00	18/04/2016 13:45:00	8138990	45283	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP012585	INGETEAM	GRID FAILURE	AK9670*69714189	WTG STOPPED DUE TO ERROR 700 -PLC. CONVERTOR COMM.FAIL. ON CHECKING THE ERROR, FOUND THAT CCU WAS IN ERROR MODE, THE ERROR CODE IS H1 AND CCU NOT CONNECTED TO LAPTOP, SO WE RESET THE CCU BY PRESSING OF RESET BUTTON IN CCU AND THEN RE-PROGRAM THE CCU FOUND OK THEN RESET THE WTG, DURING THAT TIME AGAIN CCU GOES TO ERROR MODE. HENCE FORTH WE CONFIRMED CCU WAS FAILURE. SO REPLACED THE CCU BY NEW ONE. THEN UPLOAD THE FIRMWARE AND CHECKED ERROR FREE FOUND OK. THERE AFTER WTG PUT BACK INTO OPERATION MO	DFM CCU FAILURE	AFTER GRID FAILURE	BOTTOM CONTROL PANEL	GRID FLUXUATION	INGETEAM CCU	AFTER GRID FAILURE	01 NUMBER	WTG STOPPED DUE TO ERROR 700 -PLC. CONVERTOR COMM.FAIL. ON CHECKING THE ERROR, FOUND THAT CCU WAS IN ERROR MODE, THE ERROR CODE IS H1 AND CCU NOT CONNECTED TO LAPTOP, SO WE RESET THE CCU BY PRESSING OF RESET BUTTON IN CCU AND THEN RE-PROGRAM THE CCU FOUND OK THEN RESET THE WTG, DURING THAT TIME AGAIN CCU GOES TO ERROR MODE. HENCE FORTH WE CONFIRMED CCU WAS FAILURE. SO REPLACED THE CCU BY NEW ONE. THEN UPLOAD THE FIRMWARE AND CHECKED ERROR FREE FOUND OK. THERE AFTER WTG PUT BACK INTO OPERATION MO	Assigned	ON CHECKING THE ERROR, FOUND THAT CCU WAS IN ERROR MODE, THE ERROR CODE IS H1 AND CCU NOT CONNECTED TO LAPTOP, SO WE RESET THE CCU BY PRESSING OF RESET BUTTON IN CCU AND THEN RE-PROGRAM THE CCU FOUND OK THEN RESET THE WTG, DURING THAT TIME AGAIN CCU GOES TO ERROR MODE. HENCE FORTH WE CONFIRMED CCU W	ON CHECKING THE ERROR, FOUND THAT CCU WAS IN ERROR MODE, THE ERROR CODE IS H1 AND CCU NOT CONNECTED TO LAPTOP, SO WE RESET THE CCU BY PRESSING OF RESET BUTTON IN CCU AND THEN RE-PROGRAM THE CCU FOUND OK THEN RESET THE WTG, DURING THAT TIME AGAIN CCU GOES TO ERROR MODE. HENCE FORTH WE CONFIRMED CCU WAS FAILURE. SO REPLACED THE CCU BY NEW ONE. THEN UPLOAD THE FIRMWARE AND CHECKED ERROR FREE FOUND OK. THERE AFTER WTG PUT BACK INTO OPERATION MODE. -Field Engineer-Mylsamy P. | SF.NO:- 265 SVSM 4 WTG DFM CCU FAILURE-Field Operations Manager-Dhanabal S | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Shankar Anand R.	IMG_20160418_140656973.jpg
CIR-10000540	100260077	Sri Velayudhaswamy Spinning Mills (P) Ltd.	ELAVANTHI	WF-IN-022-0833-Y1-A-016	0.85	65	Standard	Indar	20305001120	Gamesa(China)	601928	High Temperature	STD+	Standard	13/05/2010	402366376	17/05/2016	-0	Yathavaraj V	1394	1437	17/05/2016 23:30:00	17/05/2016 22:10:00	8185360	45816	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP012585	INGETEAM	NORMAL OPERATION	AK9670*69724231	700 -PLC COVERTOR COMMUNICATION ERROR.	DFM CCU FAILURE	DURING NORMAL OPERATION	BOTTOM CONTROL PANEL	GRID PROBLEM	CONVERTOR CONTROL UNI	DURING NORMAL OPERATION TIME GRID FLEXUATION	01 NUMBER	WTG STOPPED DUE TO ERROR 700 -PLC. CONVERTOR COMM.FAIL. ON CHECKING THE ERROR, FOUND THAT CCU WAS IN ERROR MODE, THE ERROR CODE IS H1 AND CCU NOT CONNECTED TO LAPTOP, SO WE RESET THE CCU BY PRESSING OF RESET BUTTON IN CCU AND THEN RE-PROGRAM THE CCU FOUND OK THEN RESET THE WTG, DURING THAT TIME AGAIN CCU GOES TO ERROR MODE. HENCE FORTH WE CONFIRMED CCU WAS FAILURE. SO REPLACED THE CCU BY NEW ONE. THEN UPLOAD THE FIRMWARE AND CHECKED ERROR FREE FOUND OK. THERE AFTER WTG PUT BACK INTO OPERATION MO		WTG STOPPED DUE TO ERROR 700 -PLC. CONVERTOR COMM.FAIL. ON CHECKING THE ERROR, FOUND THAT CCU WAS IN ERROR MODE, THE ERROR CODE IS H1 AND CCU NOT CONNECTED TO LAPTOP, SO WE RESET THE CCU BY PRESSING OF RESET BUTTON IN CCU AND THEN RE-PROGRAM THE CCU FOUND OK THEN RESET THE WTG, DURING THAT TIME AGAI
CIR-10000005	100260140	N.Sumathi	ELAVANTHI	WF-IN-022-0833-Y1-A-005	0.85	65	Standard	Indar	20305001196	Gamesa(China)	602062	High Temperature	STD+	Standard	24/07/2010	44235	11/02/2016	120-Error in Yaw pulses	Muthuraj M.	1371	1374	11/02/2016 23:34:32	11/02/2016 01:30:00	40065	4677	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP 5435	Balluff	LIGHTNING	3456	WTG feedback problem	Aux failure	high voltage	specify	grid	franklin	change balluff sensor	1	melt cable fail balluff sensor	Assigned	Checked Balluff sensor terminals | Check the supply voltage | check mcb | cntactor operation | problem solved	failure-Field Engineer-Muthuraj M. | Approved and redirected to PTS-Field Operations Manager-Dhanabal S | closed-Phone Technical Support-Senthil M. | feedback problem resolved after replaced balluff sensor-Functionality Support Lead-Shankar Anand R. | -Quality-Vijay Chinnaswamy
CIR-10000454	100260140	N.Sumathi	ELAVANTHI	WF-IN-022-0833-Y1-A-005	0.85	65	Standard	Indar	20305001196	Gamesa(China)	602062	High Temperature	STD+	Standard	24/07/2010	402332359	14/04/2016	-0	Yathavaraj V	1373	1437	14/04/2016 18:30:00	14/04/2016 11:15:00	6971310	43797	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP012531 , GP004968	EUPEC FF400R12KE3	GRID FAILURE		"WTG STOPPED DUE TO ERROR 2231.INVETER PHASE T ERROR. ON CHECKING THE ERROR FOUND THAT 2 NOS OF IGBT FAILURE IN T PHASE OF INVETER SIDE AND TOO FURTHER CHECKING FOUND THAT SCR FAILURE (ANODE TO CATHODE SHORT CIRCUIT) SO WE REPLACED THE ABOVE SAID FAILURE BY NEW ONE. THERE AFTER CHECKED THE POLE TEST FOUND OK. THEN WTG PUT BACK INTO OPERATION MODE. "	IGBT FAILURE	AFTER GRID RESUMED TIME	BOTTOM CONVERTER PANEL	AFTER GRID FAILURE	IGBT & SCR DIODE	AFTER GRID FAILURE	IGBT - 20NO'S, SCR DIODE - 01NO.	WTG STOPPED DUE TO ERROR 2231.INVETER PHASE T ERROR. ON CHECKING THE ERROR FOUND THAT 2 NOS OF IGBT FAILURE IN T PHASE OF INVETER SIDE AND TOO FURTHER CHECKING FOUND THAT SCR FAILURE (ANODE TO CATHODE SHORT CIRCUIT) SO WE REPLACED THE ABOVE SAID FAILURE BY NEW ONE. THERE AFTER CHECKED THE POLE TEST FOUND OK. THEN WTG PUT BACK INTO OPERATION MODE.	Assigned	ON CHECKING THE ERROR FOUND THAT 2 NOS OF IGBT FAILURE IN T PHASE OF INVETER SIDE AND TOO FURTHER CHECKING FOUND THAT SCR FAILURE (ANODE TO CATHODE SHORT CIRCUIT) SO WE REPLACED THE ABOVE SAID FAILURE BY NEW ONE. THERE AFTER CHECKED THE POLE TEST FOUND OK. THEN WTG PUT BACK INTO OPERATION MODE.	"WTG STOPPED DUE TO ERROR 2231.INVETER PHASE T ERROR. ON CHECKING THE ERROR FOUND THAT 2 NOS OF IGBT FAILURE IN T PHASE OF INVETER SIDE AND TOO FURTHER CHECKING FOUND THAT SCR FAILURE (ANODE TO CATHODE SHORT CIRCUIT) SO WE REPLACED THE ABOVE SAID FAILURE BY NEW ONE. THERE AFTER CHECKED THE POLE TEST FOUND OK. THEN WTG PUT BACK INTO OPERATION MODE. " -Field Engineer-Yathavaraj V | SF.NO:- 712 N.SUMATHI WTG IGBT FAILURE-Field Operations Manager-Dhanabal S | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.
CIR-10000452	100260072	Lakshmi Ring Travellers (Coimbatore) Limited	ELAVANTHI	WF-IN-022-0845-Y1-A-005	0.85	65	Standard	Indar	20305001109	Rexroth	72802005048	High Temperature	STD+	Standard	31/03/2010	402329528	12/04/2016	-0	Suresh Kumar C.A.	1373	1437	12/04/2016 15:30:11	12/04/2016 13:30:00	8454960	45309	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP004897	PHONIX CONTACT	NORMAL OPERATION		WTG STOPPED DUE TO ERROR 2118.BUS ERROR INTER BUS FAILURE. WE CHECKED THE BUS FAILURE LOG, FOUND THAT THE ERROR CODE IS 3.16 AND THIS ERROR CODE DEFINED AS AN AI 1 MODULE FAILURE. SO WE REPLACED THE ANALOG INPUT MODULE 1 BY NEW ONE. THERE AFTER WTG PUT BACK INTO OPERATION MODE.	AI 1 MODULE FAILURE	DURING NORMAL OPERATION	TOP CONTROL PANEL	MODULE FAILURE OR COPRESSING PROBLEM	ANALOG INPUT MODULE	MODULE FAILURE OR COPRESSING PROBLEM	01 NUMBER	WTG STOPPED DUE TO ERROR 2118.BUS ERROR INTER BUS FAILURE. WE CHECKED THE BUS FAILURE LOG, FOUND THAT THE ERROR CODE IS 3.16 AND THIS ERROR CODE DEFINED AS AN AI 1 MODULE FAILURE. SO WE REPLACED THE ANALOG INPUT MODULE 1 BY NEW ONE. THERE AFTER WTG PUT BACK INTO OPERATION MODE.	Assigned	AI 1 MODULE FAILURE. SO WE REPLACED THE ANALOG INPUT MODULE 1 BY NEW ONE.	WE CHECKED THE BUS FAILURE LOG, FOUND THAT THE ERROR CODE IS 3.16 AND THIS ERROR CODE DEFINED AS AN AI 1 MODULE FAILURE. SO WE REPLACED THE ANALOG INPUT MODULE 1 BY NEW ONE. THERE AFTER WTG PUT BACK INTO OPERATION MODE.-Field Engineer-Suresh Kumar C.A. | SF.NO:-441 WTG ANALOG INPUT MODULE FAILURE-Field Operations Manager-Dhanabal S | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Shankar Anand R.
CIR-10000537	100260074	Lakshmi Electrical Control Systems Limited	ELAVANTHI	WF-IN-022-0845-Y1-A-006	0.85	65	Standard	Indar	20305001119	Gamesa(China)	601914	High Temperature	STD+	Standard	31/03/2010	402361788	13/05/2016	-0	Mylsamy P.	1404	1437	13/05/2016 13:00:00	13/05/2016 22:30:00	8144970	45634	ELECTRICAL	GENERATOR SYSTEM	50051		NORMAL OPERATION		502.HIGH TEMP. ON GEN. BEAR. NDE	PT100	DURING RUNNING TIME	GENERATER	PT100 SENSOR WORN OUT	NDE BEARING TEPERATURE SENSOR	PT100 SENSOR WORN OUT	01 NUMBER	DURING RUNNING TIME WTG STOPPED DUE TO THIS ERROR. WE HAVE CHECKED AND FOUND THAT GENERATOR NDE BEARING TEMPERATURE SENSOR PT100 WAS WORN OUT CONDITION. SO REPLACED THE FAILURE SENSOR BY NEW ONE. THERE AFTER RESTART THE WTG AND SYSTEM FOUND OK.		DURING RUNNING TIME WTG STOPPED DUE TO THIS ERROR. WE HAVE CHECKED AND FOUND THAT GENERATOR NDE BEARING TEMPERATURE SENSOR PT100 WAS WORN OUT CONDITION. SO REPLACED THE FAILURE SENSOR BY NEW ONE. THERE AFTER RESTART THE WTG AND SYSTEM FOUND OK.
CIR-10000758	100260074	Lakshmi Electrical Control Systems Limited	ELAVANTHI	WF-IN-022-0845-Y1-A-006	0.85	65	Standard	Indar	20305001119	Gamesa(China)	601914	High Temperature	STD+	Standard	31/03/2010	402361788	13/05/2016	-0	Mylsamy P.	1404	1437	13/05/2016 13:00:00	13/05/2016 22:30:00	8144970	45634	ELECTRICAL	GENERATOR SYSTEM	50051		NORMAL OPERATION		502.HIGH TEMP. ON GEN. BEAR. NDE	PT100	DURING RUNNING TIME	GENERATER	PT100 SENSOR WORN OUT	NDE BEARING TEPERATURE SENSOR	PT100 SENSOR WORN OUT	01 NUMBER	DURING RUNNING TIME WTG STOPPED DUE TO THIS ERROR. WE HAVE CHECKED AND FOUND THAT GENERATOR NDE BEARING TEMPERATURE SENSOR PT100 WAS WORN OUT CONDITION. SO REPLACED THE FAILURE SENSOR BY NEW ONE. THERE AFTER RESTART THE WTG AND SYSTEM FOUND OK.		DURING RUNNING TIME WTG STOPPED DUE TO THIS ERROR. WE HAVE CHECKED AND FOUND THAT GENERATOR NDE BEARING TEMPERATURE SENSOR PT100 WAS WORN OUT CONDITION. SO REPLACED THE FAILURE SENSOR BY NEW ONE. THERE AFTER RESTART THE WTG AND SYSTEM FOUND OK.
CIR-10000531	100260075	Lakshmi Electrical Control Systems Limited	ELAVANTHI	WF-IN-022-0845-Y1-A-001	0.85	65	Standard	Indar	20305001118	Gamesa(China)	601941	High Temperature	STD+	Standard	17/04/2010	402348944	29/04/2016	-0	Mylsamy P.	1404	1437	29/04/2016 18:00:00	29/04/2016 17:30:00	8680320	45532	CONTROL SYSTEM	GENERATOR SYSTEM	50050	FLEX	NORMAL OPERATION		WTG MANUALLY STOPPED FOR GENERATOR ENCODER COUPLER REPLACEMENT WORK.	ENCODER COUPLER DAMAGED	DURING SCHEDULE SERVICE	GENERATER	COUPLER DAMAGED	ENCODER COUPLER	COUPLER PLASTIC MATERIAL DAMAGED	01 NUMBER	DURING SCHEDULE SERVICE WE FOUND THAT GENERATOR ENCODER COUPLER WAS DAMAGED CONDITION. SO WE REPLACED THE DAMAGED ENCODER COUPLER BY NEW ONE. THERE AFTER RESTART THE WTG.	Rejected	DURING SCHEDULE SERVICE WE FOUND THAT GENERATOR ENCODER COUPLER WAS DAMAGED CONDITION. SO WE REPLACED THE DAMAGED ENCODER COUPLER BY NEW ONE. THERE AFTER RESTART THE WTG.	DURING SCHEDULE SERVICE WE FOUND THAT GENERATOR ENCODER COUPLER WAS DAMAGED CONDITION. SO WE REPLACED THE DAMAGED ENCODER COUPLER BY NEW ONE. THERE AFTER RESTART THE WTG. -Field Engineer-Mylsamy P. | SF.NO:- 257 LECS 2 WTG GENERATOR ENCODER COUPLER FAILURE-Field Operations Manager-Dhanabal S | Query repeated-Phone Technical Support-Senthil M. | -Field Engineer-Mylsamy P.
CIR-10000455	100260077	Sri Velayudhaswamy Spinning Mills (P) Ltd.	ELAVANTHI	WF-IN-022-0833-Y1-A-016	0.85	65	Standard	Indar	20305001120	Gamesa(China)	601928	High Temperature	STD+	Standard	13/05/2010	402334870	18/04/2016	-0	Mylsamy P.	1373	1437	18/04/2016 14:45:00	18/04/2016 13:45:00	8138990	45283	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP012585	INGETEAM	GRID FAILURE	AK9670*69714189	WTG STOPPED DUE TO ERROR 700 -PLC. CONVERTOR COMM.FAIL. ON CHECKING THE ERROR, FOUND THAT CCU WAS IN ERROR MODE, THE ERROR CODE IS H1 AND CCU NOT CONNECTED TO LAPTOP, SO WE RESET THE CCU BY PRESSING OF RESET BUTTON IN CCU AND THEN RE-PROGRAM THE CCU FOUND OK THEN RESET THE WTG, DURING THAT TIME AGAIN CCU GOES TO ERROR MODE. HENCE FORTH WE CONFIRMED CCU WAS FAILURE. SO REPLACED THE CCU BY NEW ONE. THEN UPLOAD THE FIRMWARE AND CHECKED ERROR FREE FOUND OK. THERE AFTER WTG PUT BACK INTO OPERATION MO	DFM CCU FAILURE	AFTER GRID FAILURE	BOTTOM CONTROL PANEL	GRID FLUXUATION	INGETEAM CCU	AFTER GRID FAILURE	01 NUMBER	WTG STOPPED DUE TO ERROR 700 -PLC. CONVERTOR COMM.FAIL. ON CHECKING THE ERROR, FOUND THAT CCU WAS IN ERROR MODE, THE ERROR CODE IS H1 AND CCU NOT CONNECTED TO LAPTOP, SO WE RESET THE CCU BY PRESSING OF RESET BUTTON IN CCU AND THEN RE-PROGRAM THE CCU FOUND OK THEN RESET THE WTG, DURING THAT TIME AGAIN CCU GOES TO ERROR MODE. HENCE FORTH WE CONFIRMED CCU WAS FAILURE. SO REPLACED THE CCU BY NEW ONE. THEN UPLOAD THE FIRMWARE AND CHECKED ERROR FREE FOUND OK. THERE AFTER WTG PUT BACK INTO OPERATION MO		ON CHECKING THE ERROR, FOUND THAT CCU WAS IN ERROR MODE, THE ERROR CODE IS H1 AND CCU NOT CONNECTED TO LAPTOP, SO WE RESET THE CCU BY PRESSING OF RESET BUTTON IN CCU AND THEN RE-PROGRAM THE CCU FOUND OK THEN RESET THE WTG, DURING THAT TIME AGAIN CCU GOES TO ERROR MODE. HENCE FORTH WE CONFIRMED CCU W		IMG_20160418_140656973.jpg
CIR-10000589	100260067	Prabhu Spinning Mills (P) Ltd	ELAVANTHI	WF-IN-022-0833-Y1-A-018	0.85	65	Standard	Indar	20305001102	Gamesa(China)	601894	High Temperature	STD+	Standard	13/05/2010	402369210	21/05/2016	-0	Suresh Kumar C.A.	1404	1437	21/05/2016 18:30:00	21/05/2016 17:00:00	7956980	45933	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP004890	PHONIX CONTACT	GRID FAILURE	1113670120	2118.BUS ERROR INTER BUS FAILURE & 411.HIGH BRAKE ON TEMPERATURE
CIR-10000687	100260067	Prabhu Spinning Mills (P) Ltd	ELAVANTHI	WF-IN-022-0833-Y1-A-018	0.85	65	Standard	Indar	20305001102	Gamesa(China)	601894	High Temperature	STD+	Standard	13/05/2010	402369210	21/05/2016	-0	Suresh Kumar C.A.	1404	1437	21/05/2016 18:30:00	21/05/2016 17:00:00	7956980	45933	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP004890	PHONIX CONTACT	GRID FAILURE	1113670120	2118.BUS ERROR INTER BUS FAILURE & 411.HIGH BRAKE ON TEMPERATURE	DIGITAL MODULE	AFTER GRID FAILURE	TOP CONTROL PANEL	MODULE FAILURE	D/O MODULE	AFTER GRID FAILURE	01 NUMBER	AFTER GRID RESUMED, WTG STOPPED DUE TO ERROR 2118.BUS ERROR INTER BUS FAILURE. WE CHECKED THE BUS FAILURE LOG, FOUND THAT THE ERROR CODE DEFINED AS A SD1 MODULE FAILURE AND TOO BRAKE PAD WITH THERMISTOR OPENED CONDITION. SO WE REPLACED THE SD1 MODULE AND BRAKE PAD WITH THERMISTOR BY NEW ONE. THERE AFTER WTG PUT BACK INTO OPERATION MODE.		AFTER GRID RESUMED, WTG STOPPED DUE TO ERROR 2118.BUS ERROR INTER BUS FAILURE. WE CHECKED THE BUS FAILURE LOG, FOUND THAT THE ERROR CODE DEFINED AS A SD1 MODULE FAILURE AND TOO BRAKE PAD WITH THERMISTOR OPENED CONDITION. SO WE REPLACED THE SD1 MODULE AND BRAKE PAD WITH THERMISTOR BY NEW ONE. THERE A
CIR-10000538	100260071	Vetal Textiles & Electronics Pvt. Ltd.	ELAVANTHI	WF-IN-022-0833-Y1-A-006	0.85	65	Standard	Indar	20305001088	Gamesa(China)	601899	High Temperature	STD+	Standard	11/05/2010	402367727	20/05/2016	-0	Suresh Kumar C.A.	1404	1437	20/05/2016 10:30:00	20/05/2016 09:30:00	7140990	45558	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP062661	MAGELIS XBTGT2220 TELEMECHANIC	GRID FAILURE	085948F012315	2107 - PLC INITILIZATION FAILURE
CIR-10000539	100260071	Vetal Textiles & Electronics Pvt. Ltd.	ELAVANTHI	WF-IN-022-0833-Y1-A-006	0.85	65	Standard	Indar	20305001088	Gamesa(China)	601899	High Temperature	STD+	Standard	11/05/2010	402367727	20/05/2016	-0	Suresh Kumar C.A.	1404	1437	20/05/2016 10:30:00	20/05/2016 09:30:00	7140990	45558	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP062661	MAGELIS XBTGT2220 TELEMECHANIC	GRID FAILURE	085948F012315	2107 - PLC INITILIZATION FAILURE	TOUCH SCREEN	AFTER GRID FAILURE	BOTTOM CONTROL PANEL	AFTER GRID FAILURE	TOUCH SCREEN DISPLAY	AFTER FEEDER LOAD SHEDDING	01 NUMBER	"AFTER GRID RESUMED, WTG STOPPED DUE TO ERROR 2107 - PLC INITIALIZATION FAILURE. WE CHECKED AND FOUND THAT PLC WAS HANG AND TOO TOUCH SCREEN WAS NOT ON EVEN THOUGH 24V SUPPLY AVAILABLE. SO WE RE-PROGRAM THE PLC AND UPLOAD THE PARAMETER AND THEN REPLACED THE TOUCH SCREEN BY NEW ONE. THERE AFTER RESET THE WTG AND FOUND SYSTEM OK. "		"AFTER GRID RESUMED, WTG STOPPED DUE TO ERROR 2107 - PLC INITIALIZATION FAILURE. WE CHECKED AND FOUND THAT PLC WAS HANG AND TOO TOUCH SCREEN WAS NOT ON EVEN THOUGH 24V SUPPLY AVAILABLE. SO WE RE-PROGRAM THE PLC AND UPLOAD THE PARAMETER AND THEN REPLACED THE TOUCH SCREEN BY NEW ONE. THERE AFTER RESE
CIR-10000588	100260071	Vetal Textiles & Electronics Pvt. Ltd.	ELAVANTHI	WF-IN-022-0833-Y1-A-006	0.85	65	Standard	Indar	20305001088	Gamesa(China)	601899	High Temperature	STD+	Standard	11/05/2010	402367727	20/05/2016	-0	Suresh Kumar C.A.	1404	1437	20/05/2016 10:30:00	20/05/2016 09:30:00	7140990	45558	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP062661	MAGELIS XBTGT2220 TELEMECHANIC	GRID FAILURE	085948F012315	2107 - PLC INITILIZATION FAILURE	TOUCH SCREEN	AFTER GRID FAILURE	BOTTOM CONTROL PANEL	AFTER GRID FAILURE	TOUCH SCREEN DISPLAY	AFTER FEEDER LOAD SHEDDING	01 NUMBER	"AFTER GRID RESUMED, WTG STOPPED DUE TO ERROR 2107 - PLC INITIALIZATION FAILURE. WE CHECKED AND FOUND THAT PLC WAS HANG AND TOO TOUCH SCREEN WAS NOT ON EVEN THOUGH 24V SUPPLY AVAILABLE. SO WE RE-PROGRAM THE PLC AND UPLOAD THE PARAMETER AND THEN REPLACED THE TOUCH SCREEN BY NEW ONE. THERE AFTER RESET THE WTG AND FOUND SYSTEM OK. "	Deleted	"AFTER GRID RESUMED, WTG STOPPED DUE TO ERROR 2107 - PLC INITIALIZATION FAILURE. WE CHECKED AND FOUND THAT PLC WAS HANG AND TOO TOUCH SCREEN WAS NOT ON EVEN THOUGH 24V SUPPLY AVAILABLE. SO WE RE-PROGRAM THE PLC AND UPLOAD THE PARAMETER AND THEN REPLACED THE TOUCH SCREEN BY NEW ONE. THERE AFTER RESE
CIR-10000451	100260076	Sri Shanmugavel Mills (P) Ltd.	ELAVANTHI	WF-IN-022-0833-Y2-A-004	0.85	65	Standard	Indar	20305001116	Gamesa(China)	601940	High Temperature	STD+	Standard	29/03/2010	402327377	10/04/2016	-0	Suresh Kumar C.A.	1370	1437	10/04/2016 11:30:00	10/04/2016 10:15:00	8892180	45639	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	9000601	NRG	NORMAL OPERATION	GP939-3-S	WTG STOPPED DUE TO ERROR 300 â€“ ANEMOMETER FAILURE. ON CHECKING THE ERROR FOUND THAT ANEMOMETER WAS STRUCK UP DUE TO ANEMOMETER BEARING FAILURE, SO WE REPLACED THE ANEMOMETER BY NEW ONE. THERE AFTER WTG PUT BACK INTO OPERATION MODE.	ANEMOMETER BEARING FAILURE	DURING NORMAL OPERATION	ANEMOMETER	BEARING STRUCK UP	ANEMOMETER	BAERING STRUCK UP	01 NUMBER	WTG STOPPED DUE TO ERROR 300 â€“ ANEMOMETER FAILURE. ON CHECKING THE ERROR FOUND THAT ANEMOMETER WAS STRUCK UP DUE TO ANEMOMETER BEARING FAILURE, SO WE REPLACED THE ANEMOMETER BY NEW ONE. THERE AFTER WTG PUT BACK INTO OPERATION MODE.	Assigned	ANEMOMETER WAS STRUCK UP DUE TO ANEMOMETER BEARING FAILURE, SO WE REPLACED THE ANEMOMETER BY NEW ONE. T	ON CHECKING THE ERROR FOUND THAT ANEMOMETER WAS STRUCK UP DUE TO ANEMOMETER BEARING FAILURE, SO WE REPLACED THE ANEMOMETER BY NEW ONE. THERE AFTER WTG PUT BACK INTO OPERATION MODE. -Field Engineer-Suresh Kumar C.A. | SF .NO:- 659 NORTH WTG ANOMOMETER FAILUTRE-Field Operations Manager-Dhanabal S | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Shankar Anand R.
CIR-10000590	100260066	Sivaraj Spinning Mills (P) Limited	ELAVANTHI	WF-IN-022-0833-Y1-A-013	0.85	65	Standard	Indar	20305001100	Gamesa(China)	601889	High Temperature	STD+	Standard	17/04/2010	402379274	31/05/2016	-0	Suresh Kumar C.A.	1404	1437	31/05/2016 18:30:00	31/05/2016 17:30:00	8357660	46195	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP062661	MAGELIS XBTGT2220 TELEMECHANIC	GRID FAILURE	085948F010540	2107 - PLC INITILIZATION FAILURE	TOUCH SCREEN	AFTER GRID FAILURE	BOTTOM CONTROL PANEL	GRID FAILURE	OPRATION DISPLAY	AFTER GRID DUE TO THIS ERROR	01 NUMBER	"AFTER GRID RESUMED, WTG STOPPED DUE TO ERROR 2107 - PLC INITIALIZATION FAILURE. WE CHECKED AND FOUND THAT PLC WAS HANG AND TOO TOUCH SCREEN WAS NOT ON EVEN THOUGH 24V SUPPLY AVAILABLE. SO WE RE-PROGRAM THE PLC AND UPLOAD THE PARAMETER AND THEN REPLACED THE TOUCH SCREEN BY NEW ONE. THERE AFTER RESET THE WTG AND FOUND SYSTEM OK. "	Assigned	"AFTER GRID RESUMED, WTG STOPPED DUE TO ERROR 2107 - PLC INITIALIZATION FAILURE. WE CHECKED AND FOUND THAT PLC WAS HANG AND TOO TOUCH SCREEN WAS NOT ON EVEN THOUGH 24V SUPPLY AVAILABLE. SO WE RE-PROGRAM THE PLC AND UPLOAD THE PARAMETER AND THEN REPLACED THE TOUCH SCREEN BY NEW ONE. THERE AFTER RESE	"AFTER GRID RESUMED, WTG STOPPED DUE TO ERROR 2107 - PLC INITIALIZATION FAILURE. WE CHECKED AND FOUND THAT PLC WAS HANG AND TOO TOUCH SCREEN WAS NOT ON EVEN THOUGH 24V SUPPLY AVAILABLE. SO WE RE-PROGRAM THE PLC AND UPLOAD THE PARAMETER AND THEN REPLACED THE TOUCH SCREEN BY NEW ONE. THERE AFTER RESET THE WTG AND FOUND SYSTEM OK. " -Field Engineer-Suresh Kumar C.A. | SF.NO:- 71/2 SUPER SALES 2 WTG 230V/2.5AMPS POWER SUPPLY UNIT FAILURE-Field Operations Manager-Dhanabal S | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Shankar Anand R.
CIR-10000317	100260079	Subam Papers (P) Ltd	Theni-Kadamalaigundu	WF-IN-022-0846-Y2-A-010	0.85	65	Standard	Indar	20305001122	Gamesa(China)	601930	High Temperature	STD+	Standard	30/06/2010	402343190	17/04/2016	3409-Line Protection Triggered	Devasudar Singh	1404	1440	17/04/2016 23:30:00	17/04/2016 22:00:00	8220120	42233	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP188019	SAFETEC	NORMAL OPERATION		Wtg stopped due to error no:3409 Line protection tripped. we check & found surge arrestor got failed.	Surge arrestor failure	Breakdown	SF.NO:635(SUBAM)	Continuous operation	S.Johnpeter, S.Vijayakumar	We replaced surge arrestor	01no	Continuous operation	Assigned	we replaced new surge arrestor .	Wtg stopped due to error no:3409 Line protection tripped. we check & found surge arrestor got failed.so we replaced by new one.-Field Engineer-John Peter S | Problem solved-Field Operations Manager-Devasudar Singh | BOP Auditing recommended-Phone Technical Support-Senthil M. | Type I Surge Arrester installation to be planned in theni WF-Functionality Support Lead-Murugesan P. | -Functionality Support Specialist-Mayank	IMG_20160208_204037.jpg
CIR-10000337	100260081	Subam Papers (P) Ltd	Theni-Kadamalaigundu	WF-IN-022-0846-Y2-A-009	0.85	65	Standard	Indar	20305001112	Gamesa(China)	601925	High Temperature	STD+	Standard	12/04/2010	402348800	30/04/2016	210-Brake drive error	Devasudar Singh	1404	1440	30/04/2016 17:30:00	30/04/2016 16:30:00	8662880	42822	MECHANICAL	GENERATOR SYSTEM	50591	GAMESA	NORMAL OPERATION		During service time we check & found Phase carbon brush 01 no warn out.	Phase carbon brush warn out	During service time	SF.NO:627(SUBAM)	Continuous operation	R.Dineshbabu, M.Vinumonikandan, S.Vijayakumar	we replaced phase carbon brush	01no	Continuous operation	Assigned	we replaced phase carbon brush by new one.	During service time we check & found Phase carbon brush 01 no warn out.we replaced by new one.-Field Engineer-Dinesh Babu R. | Problem solved-Field Operations Manager-Devasudar Singh | closed - CIR not required for consumable Items-Phone Technical Support-Senthil M. | Closed-Functionality Support Lead-Murugesan P. | -Quality-Vijay Chinnaswamy	Carbon brush.jpg Carbon brush
CIR-10000193	100260085	BMM Paper Board (P) Ltd	Theni-Kadamalaigundu	WF-IN-022-0846-Y2-A-008	0.85	65	Standard	Indar	20305001108	Gamesa(China)	601957	High Temperature	STD+	Standard	19/05/2010		28/03/2016	-0	Dinesh Babu R.	1404	1440	28/03/2016 14:45:00	28/03/2016 11:00:00	7851100	41930	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP012585,GP012532,GP012531,GP188019,50074,50071	INGETEAM, SAFETEC,ABB,EUPEC	NORMAL OPERATION	2263112547,116068170,56465005686,69721392	Wtg stopped due to error no:2231 Error in 'T'phase inverter. we check & found bypass contactor (KM52R) failure & surge arrestor blast, 12no's IGBT failure,02no's driver card failure, after reseting time, error no:2229 error in 'R' phase inverter, we check & found CCU, 01no driver card, crowbar card, bypass contactor Addn.block failure.	CCU,IGBT,Drivercard, Crowbarcard,bypass contactor failure.	Breakdown	SF.NO:646(BMM)	Grid failure, surge fault, continuous operation.	R.Dineshbabu, S.Johnpeter, M.Vinu, G.Bala	CCU,IGBT,Drivercard, Crowbarcard,bypass contactor replaced all by new one.	01no, 12no's, 03no's, 01no	Grid failure, surge fault, continuous operation.	Assigned	we replaced all materials by new one.	Wtg stopped due to error no:2231 Error in 'T'phase inverter. we check & found bypass contactor (KM52R) failure & surge arrestor blast, 12no's IGBT failure,02no's driver card failure, after reseting time, error no:2229 error in 'R' phase inverter, we check & found CCU, 01no driver card, crowbar card, bypass contactor Addn.block failure.we replaced all by new one.-Field Engineer-Dinesh Babu R. | Problem solved-Field Operations Manager-Devasudar Singh | BOP Auditing recommended-Phone Technical Support-Senthil M. | BOP audit and converter dust level to be verfied-Functionality Support Lead-Murugesan P. | PQ audit to be conducted at this WF. Dust sensor trial can be conducted at this WTG.-Functionality Support Specialist-Mayank | closed-Quality-Vijay Chinnaswamy | -Functionality Support Specialist-Selvamani K.	IMG_20160328_111837.jpg Bypass contactor | IMG_20160328_111906.jpg Drivercard | IMG_20160328_172643.jpg IGBT | IMG_20160329_095047.jpg CCU | IMG_20160328_173013.jpg Capacitor
CIR-10000535	100260198	HINDUSTAN HARDWARES	Theni-Kadamalaigundu	WF-IN-022-0872-Y2-A-007	0.85	65	Standard	Indar	20305001248	Gamesa(China)	602202	High Temperature	STD+	Standard	28/09/2010	402372310	24/05/2016	-0	Avudaippan M	1404	1440	24/05/2016 18:00:00	24/05/2016 14:00:00	6701030	40465	MECHANICAL	BLADE BEARING SYSTEM	P630694	DYSTA	NORMAL OPERATION		WTG Manually stopped for blade hub joint broken bolt replacement work We replaced M24X180 broken bolt 2noâ€™s replaced it(Blade no:C, Pos:13,15)	Blade bearing bolt broken	Visual inspection work	SF.NO:364	Continuous grid drop	M.Avudaiappan, T.Stalinkumar, S.Vijayakumar	we replaced new bolt	05no's	Continuous grid drop	Assigned	We replaced M24X180 broken bolt 2noâ€™s replaced it(Blade no:C, Pos:13,15) We installed new bolt and restarted it WTG.	WTG Manually stopped for blade hub joint broken bolt replacement work ,We replaced M24X180 broken bolt 2noâ€™s replaced it(Blade no:C, Pos:13,15) . We installed new bolt and restarted it WTG.-Field Engineer-Avudaippan M | Problem solved-Field Operations Manager-Devasudar Singh | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Anand A.P	Blade bearing bolt.jpg Blade bearing bolt
CIR-10000277	100260176	ARKAY ENERGY (RAMESWARAM) LIMITED	Theni-Kadamalaigundu	WF-IN-022-0872-Y2-A-004	0.85	65	Standard	Indar	20305001238	Gamesa(China)	602170	High Temperature	STD+	Standard	29/03/2011	402329119	11/04/2016	411-High brake temperature	Devasudar Singh	1404	1440	11/04/2016 17:30:00	11/04/2016 16:30:00	8032800	36298	MECHANICAL	NACELLE INSTRUMENTATION SYSTEM	P370104, P393462	GAMESA, ABB	NORMAL OPERATION		During service time error no:411 high brake temp, error no:206 Hu.protection tripped, we check & found brakepad with out thermistor(05no's) warnout, hyd.contactor failure.	Brake pad, Hyd.contactor failure	During service time.	Sf.No:501(JATTIN)	Continuous operation	D.Yukesh, G.Balasubramanian	Brake pad, Hyd.contactor replaced by new one.	05no's, 01no	Continuous operation, Grid drop	Assigned	We replaced normal brake pad & hyd.contactor by new one.	During service time error no:411 high brake temp, error no:206 Hu.protection tripped, we check & found brakepad with out thermistor(05no's) warnout, hyd.contactor failure.we replaced all by new one.-Field Engineer-Balasubramanian G. | Problem solved-Field Operations Manager-Devasudar Singh	Brake pad.jpg Brake pad | IMG_20160202_164656_HDR.jpg Hyd.contactor
CIR-10000601	100260156	Shiny Knitwear (P) Ltd.	Theni-Kadamalaigundu	WF-IN-022-0872-Y2-A-006	0.85	65	Standard	Indar	20305001217	Gamesa(China)	602098	High Temperature	STD+	Standard	28/09/2010	402390198	08/06/2016	-0	Devasudar Singh	1404	1440	08/06/2016 17:00:00	08/06/2016 15:40:00	7971380	40667	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP012585	INGETEAM	NORMAL OPERATION	226642328	WTG stopped due to error no:2216 Control module over heat. We checked and found that CCU internal problem	CCU failure	Breakdown	SF.NO:533(SHINY)	Grid drop, Grid Fluctuations, Software problem Grid Fluctuation	D.Yukesh, A.Parasuraman	we replaced CCU by new one.	01no	Grid drop, Grid Fluctuations, Software problem Grid Fluctuation	Assigned	We checked and found that CCU internal problem We replaced CCU and start the WTG	WTG stopped due to error no:2216 Control module over heat.We checked and found that CCU internal problem. We replaced CCU and start the WTG-Field Engineer-Yukesh D. | Problem soilved-Field Operations Manager-Devasudar Singh | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Shankar Anand R.	IMG_20160609_102221.jpg CCU
CIR-10000549	100260162	CHERAN SPINNER LIMITED	Theni-Kadamalaigundu	WF-IN-022-0872-Y2-A-001	0.85	65	Standard	Indar	20305001201	Gamesa(China)	602120	High Temperature	STD+	Standard	28/09/2010	402378422	30/05/2016	-0	Stalin Kumar T	1404	1440	30/05/2016 22:00:00	30/05/2016 19:00:00	7901860	40792	MECHANICAL	BLADE BEARING SYSTEM	P630694	DYSTA	NORMAL OPERATION		WTG Manually stopped for Visual inspection work that time we found blade bearing broken bolt replacement work. We replaced M24X180 broken bolt 5 noâ€™s replaced it(Blade no:A ,POS 3,4,5,6,7)	Blade bearing bolt broken	During visual inspection work	SF.NO:375	Material defect ,wrong thread Quality issue, exceeded to torque limit	T.Stalinkumar, M.Avudaiappan, M.Vinu	We replaced broken bolts	8no's	Material defect ,wrong thread Quality issue, exceeded to torque limit	Assigned	We replaced M24X180 broken bolt 5 noâ€™s replaced it(Blade no:A ,POS 3,4,5,6,7). We installed new bolt and restarted it WTG.	WTG Manually stopped for Visual inspection work that time we found blade bearing broken bolt replacement work. We replaced M24X180 broken bolt 5 noâ€™s replaced it(Blade no:A ,POS 3,4,5,6,7). We installed new bolt and restarted it WTG.-Field Engineer-Stalin Kumar T | Problem solved-Field Operations Manager-Devasudar Singh | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Anand A.P	Blade bearing bolt.jpg Blade bearing bolts
CIR-10000290	100260198	HINDUSTAN HARDWARES	Theni-Kadamalaigundu	WF-IN-022-0872-Y2-A-007	0.85	65	Standard	Indar	20305001248	Gamesa(China)	602202	High Temperature	STD+	Standard	28/09/2010	402334038	15/04/2016	-0	Devasudar Singh	1404	1440	15/04/2016 03:30:00	15/04/2016 01:30:00	6655270	39671	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	50067	PHONIEX	NORMAL OPERATION		wtg stopped due to error no:2227 IGBT's power supply failure. so we check & found IGBT driver supply failure.	IGBT's power supply failure.	Breakdown	SF.NO:364(HINDUSTAN)	Continuous operation	S.Johnpeter, S.Vijayakumar	Power supply replaced by new one	01no	Continuous operation,grid drop	Assigned	we replaced new IGBT's power supply.	wtg stopped due to error no:2227 IGBT's power supply failure. so we check & found IGBT driver supply failure.we replaced by new power supply.-Field Engineer-John Peter S | Problem solved-Field Operations Manager-Devasudar Singh | BOP Auditing recommended-Phone Technical Support-Senthil M. | please check DM is available for Driver card failure control-Functionality Support Lead-Murugesan P. | -Functionality Support Specialist-Mayank	IMG_20160319_122737.jpg Powersupply
CIR-10000297	100260198	HINDUSTAN HARDWARES	Theni-Kadamalaigundu	WF-IN-022-0872-Y2-A-007	0.85	65	Standard	Indar	20305001248	Gamesa(China)	602202	High Temperature	STD+	Standard	28/09/2010	402334452	16/04/2016	-0	Yukesh D.	1404	1440	16/04/2016 17:30:00	16/04/2016 16:30:00	6655320	36695	MECHANICAL	ELECTRICAL CABINET SYSTEM	P370104	GAMESA	NORMAL OPERATION		During service time we check & found normal brake pads warn out.	Brake pad warnout	During service time	SF.NO:364(HINDUSTAN)	Continuous operation, material defect	D.Yukesh, M.Vinu, T.Stalkinkumar	We replaced new brake pads	04no's	Continuous operation, Material defect	Assigned	we replaced 04no's normal brake pads by new one.	During service time we check & found normal brake pads warn out.we replaced new brake pad.-Field Engineer-Yukesh D. | Problem solved-Field Operations Manager-Devasudar Singh | OK, Consumables-Phone Technical Support-Senthil M. | Brake pad failure due to continous operation. Issue closed.-Functionality Support Lead-Anand A.P | check 100% brake pad condition of WTG in this park, irrespective maintenance cycle . please follow up thoroughly.....-Quality-Vijay Chinnaswamy | Mail sent to Deva to check 100% brake pad condition-Functionality Support Lead-Anand A.P | -Quality-Vijay Chinnaswamy	Brake pad.jpg Brake pad
CIR-10000551	100260158	Sri Iyyan Textile Mills (P) Ltd	Theni-Kadamalaigundu	WF-IN-022-0846-Y2-A-005	0.85	65	Standard	Indar	20305001179	Gamesa(China)	602109	High Temperature	STD+	Standard	13/08/2010	402380976	13/05/2016	-0	Devasudar Singh	1404	1440	01/06/2016 19:15:00	13/05/2016 10:00:00	7486450	41867	MECHANICAL	BLADES			LIGHTNING		Wtg manually stopped for blade 'B' repair work	Blade 'B' repair work	During inspection	SF.NO:278	Lightening	S.Sundar, K.Sankaranarayanan, G.Senthilkannan.	Blade 'B' repair work completed		Lightening strike	Assigned	Blade 'B' repair work completed	wtg manually stopped for Blade 'B' repair work completed-Field Engineer-Dinesh Babu R. | Blade repair work completed-Field Operations Manager-Devasudar Singh | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Anand A.P
CIR-10000356	100260431	KHATAU NARBHERAM & CO	Theni-Srirangapuram	WF-IN-022-0835-Y3-A-018	0.85	65	Standard	Gamesa wind Tianjin, China	801001161	Gamesa(China)	602466	High Temperature	STD+	Standard	27/09/2011	402338821	18/04/2016	-0	Dinesh Babu R.	1404	1439	20/04/2016 18:00:00	18/04/2016 09:00:00	6202130	31488	MECHANICAL	BLADES			LIGHTNING		Wtg manual stop for blade repair work.we repaired Blade A,B,C Diverter strip replaced & Blade B Tip repair work done.	Blade problem		SF.NO:220(ATHA)	Lightening	S.Sundar, Raja,Mishra	Blade repair work done		Due to lightening		Blade A,B,C Diverter strip replaced & Blade B Tip repair work done.
CIR-10000152	100260425	K.P.R. Mill Ltd	Theni-Srirangapuram	WF-IN-022-0835-Y2-A-010	0.85	65	Standard	Gamesa wind Tianjin, China	801001167	Gamesa(China)	602448	High Temperature	STD+	Standard	30/08/2011	402308359	18/03/2016	210-Brake drive error	Devasudar Singh	1404	1439	18/03/2016 17:30:00	18/03/2016 16:30:00	6558830	32885	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	109882, P370104, GP019699	OLEAR, GAMESA, ABB	NORMAL OPERATION
CIR-10000086	100260430	KHIVRAJ MOTOR COMPANY	Theni-Srirangapuram	WF-IN-022-0835-Y1-A-004	0.85	65	Standard	Gamesa wind Tianjin, China	801001160	Gamesa(China)	602453	High Temperature	STD+	Standard	30/08/2011	402285576	01/03/2016	-0	Devasudar Singh	1403	1425	03/01/2016 03:00:22	03/01/2016 01:00:22	6309260	32272	CONTROL SYSTEM	NACELLE INSTRUMENTATION SYSTEM	GP004895	PHONIEX	NORMAL OPERATION	1114151303										Deleted
CIR-10000667	100260514	RV Consulting Service Private Limited	PETHAPPAMPATTI	WF-IN-022-0853-Y0-A-022	0.85	65	Standard	Gamesa wind Tianjin, China	801001249	Gamesa(China)	602532	High Temperature	STD+	Standard	24/03/2012	402366344	17/05/2016	-0	Jeevanandam S.	1402	1439	17/05/2016 06:00:00	17/05/2016 04:00:00	6461290	32559	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	880162	VICKERS	NORMAL OPERATION		Proportional valve replacement work								Proportional valve failure	Applied	WTG stopped due to proportional valve replacement work while checking we found WTG not goes to RUN mode and pitching was not moving to 83 degree in pause mode so we replace the Proportionala valve	WTG restarted normally -Field Engineer-Jeevanandam S. | -Field Operations Manager-Arumugam M.
CIR-10000642	100260345	Devendran Coal International Private Limited	PETHAPPAMPATTI	WF-IN-022-0853-Y3-A-003	0.85	65	Standard	Gamesa wind Tianjin, China	801001076	Gamesa(China)	602415	High Temperature	STD+	Standard	31/03/2011	402367346	19/05/2016	-0	Sorna Raja G.	1402	1439	19/05/2016 16:00:00	19/05/2016 14:00:00	7228260	40695	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP002750	semikron	NORMAL OPERATION		WTG Stopped due to 3210 - Skip error rotor invrtor phase 2 error								Rotor skip failure	Applied	so we checked the related connections and then we conform that rotor skip L2 was railure. so we replace the same	WTG restarted normally -Field Engineer-Sorna Raja G. | -Field Operations Manager-Sureshkumar K
CIR-10000254	100260153	HINDUSTAN SPINNERS B UNIT	Theni-Kadamalaigundu	WF-IN-022-0872-Y2-A-002	0.85	65	Standard	Indar	20305001205	Gamesa(Spain)	300028	High Temperature	STD+	Standard	28/09/2010	402324749	06/04/2016	-0	Devasudar Singh	1404	1440	06/04/2016 17:30:00	06/04/2016 17:00:00	7433810	39710	ELECTRICAL	NACELLE INSTRUMENTATION SYSTEM	P393462	ABB	NORMAL OPERATION		During service time error no:206 Hu.protection tripped error occur , so we check & found KM280 hyd.contactor failure, so we replaced by new one.	KM280 Hyd.contactor failure	During service time.	SF.NO:402(Hindustan)	Continuous operation	K.Sankar, G.senthilkannan, G.Bala	KM280 hyd.contactor replaced by new one.	01no	Continuous operation, Grid drop	Assigned	KM280 Hyd.contactor replaced by new one.	During service time error no:206 Hu.protection tripped error occur , so we check & found KM280 hyd.contactor failure, so we replaced by new one.-Field Engineer-Senthil Kannan G | Problem solved-Field Operations Manager-Devasudar Singh | Closed-Phone Technical Support-Senthil M. | closed-Functionality Support Lead-Murugesan P. | -Quality-Vijay Chinnaswamy	IMG_20160202_164656_HDR.jpg A26-30-10 Contactor
CIR-10000105	100260182	HINDUSTAN TEXTILES	Theni-Kadamalaigundu	WF-IN-022-0872-Y2-A-005	0.85	65	Standard	Indar	20305001239	Gamesa(China)	602161	High Temperature	STD+	Standard	28/09/2010	402300736	12/03/2016	2112-TOP supply failure	Devasudar Singh	1404	1440	12/03/2016 17:00:00	12/03/2016 10:00:00	7932680	39232	MECHANICAL	ELECTRICAL CABINET SYSTEM	1094574, GP020417	GAMESA, JAURE	NORMAL OPERATION		During generator alignment work time we found top battery back up failure & also Coupling Arm replaced.	Battery back up, Coupling arm failure	During Generator alignment time	SF.NO:570(HINDUSTAN)	Continuous operation, Grid drop	M.Vinu, S.Johnpeter, A.Parasuraman	Battery back up, Coupling arm failure , so we replaced by new one	Each 01no	Continuous operation, Grid drop	Assigned	We replaced Battery back up & coupling ARM	Problem solved-Field Engineer-John Peter S | Problem solved-Field Operations Manager-Devasudar Singh | solved-Phone Technical Support-Senthil M. | problem solved-Functionality Support Lead-Shankar Anand R. | -Quality-Vijay Chinnaswamy	IMG_20160309_233122.jpg Battery back up
CIR-10000257	100260182	HINDUSTAN TEXTILES	Theni-Kadamalaigundu	WF-IN-022-0872-Y2-A-005	0.85	65	Standard	Indar	20305001239	Gamesa(China)	602161	High Temperature	STD+	Standard	28/09/2010	402328180	08/04/2016	-0	Devasudar Singh	1404	1440	08/04/2016 17:30:00	08/04/2016 16:30:00	7947850	39846	ELECTRICAL	NACELLE INSTRUMENTATION SYSTEM	REL0068	FINDER	NORMAL OPERATION		During service time error no 2118 Interbus error occur, we check & found Top timer got failed.	Top timer got failed	During service time	SF.NO:570(Hindustan)	Continuous operation	M.Vinu, G.Bala, T.Stalinkumar	Top timer replaced by new one.	01no	Continuous operation,	Assigned	We replaced new timer & restart the turbine	During service time error no 2118 Interbus error occur, we check & found Top timer got failed. so we replaced by new timer-Field Engineer-Balasubramanian G. | Problem solved-Field Operations Manager-Devasudar Singh	IMG_20160212_072340.jpg Top timer
CIR-10000548	100260182	HINDUSTAN TEXTILES	Theni-Kadamalaigundu	WF-IN-022-0872-Y2-A-005	0.85	65	Standard	Indar	20305001239	Gamesa(China)	602161	High Temperature	STD+	Standard	28/09/2010	402374596	26/05/2016	-0	Avudaippan M	1404	1440	26/05/2016 16:00:00	26/05/2016 13:00:00	8053030	40836	MECHANICAL	BLADE BEARING SYSTEM	P630694	DYSTA	NORMAL OPERATION		WTG Manually stopped for blade hub joint broken bolt replacement work. We replaced M24X180 broken bolt 5 noâ€™s replaced it(Blade no:A ,POS 3,4,5,6,7)	Blade bearing bolt broken	During visual inspection time.	SF.NO:570	Material defect ,wrong thread Quality issue, exceeded to torque limit	M.Avudaiappan, S.Vijayakumar	we replaced blade bearing broken bolts	11no's	Material defect ,wrong thread Quality issue, exceeded to torque limit	Assigned	We replaced M24X180 broken bolt 5 noâ€™s replaced it(Blade no:A ,POS 3,4,5,6,7) We installed new bolt and restarted it WTG.	WTG Manually stopped for blade hub joint broken bolt replacement work. We replaced M24X180 broken bolt 5 noâ€™s replaced it(Blade no:A ,POS 3,4,5,6,7) . We installed new bolt and restarted it WTG.-Field Engineer-Avudaippan M | Problem solved-Field Operations Manager-Devasudar Singh | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Anand A.P	Blade bearing bolt1.jpg Blade bearing bolt
CIR-10000258	100260156	Shiny Knitwear (P) Ltd.	Theni-Kadamalaigundu	WF-IN-022-0872-Y2-A-006	0.85	65	Standard	Indar	20305001217	Gamesa(China)	602098	High Temperature	STD+	Standard	28/09/2010	402328182	08/04/2016	2118-Interbus bus error	Devasudar Singh	1404	1440	08/04/2016 17:30:00	08/04/2016 16:30:00	7766570	39430	CONTROL SYSTEM	NACELLE INSTRUMENTATION SYSTEM	REL0068	FINDER	NORMAL OPERATION		During service time error no:2118 Inter bus error occur. we check & found top timer got failed.	top timer failure	During service time.	SF.NO:533(Shiny)	Continuous operation	D.Yukesh, J.Kalimuthu, K.Ramesh	Top timer replaced by new one.	01no	Continuous operation,	Assigned	We replaced new timer & restart the timer	During service time error no:2118 Inter bus error occur. we check & found top timer got failed.so we replaced by new one.-Field Engineer-Yukesh D. | Problem solved-Field Operations Manager-Devasudar Singh	IMG_20160316_094953.jpg Timer
CIR-10000106	100260090	Rajashree Spintex Pvt. Ltd.	Theni-Kadamalaigundu	WF-IN-022-0846-Y2-A-004	0.85	65	Standard	Indar	20305001149	Gamesa(China)	601936	High Temperature	STD+	Standard	22/05/2010		14/03/2016	-0	John Peter S	1404	1440	14/03/2016 23:45:00	14/03/2016 22:00:00	8454240	41711	ELECTRICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	GP004897, 109534, 109537	PHONIEX	NORMAL OPERATION		Wtg stopped due to error no:2114 Analog card failure & 115 Yaw brake pressure high. So we check & found RV8 valve & pressure transducer & also AI2 module failure.	AI2 module, Pressure trans ducer, RV8 valve problem	Breakdown	SF.NO:224(RAJASHREE)	Continuous operation, frequent Grid drop	S.Johnpeter, T.Stalinkumar	AI2 module, Pressure transducer, RV8 valve replaced by new one.	Each 01 no	Continuous operation, frequent Grid drop,	Assigned	we check & found RV8 valve & pressure transducer & also AI2 module failure. so we replaced all by new one.	Wtg stopped due to error no:2114 Analog card failure & 115 Yaw brake pressure high. So we check & found RV8 valve & pressure transducer & also AI2 module failure.we replaced all by newone. Now problem solved-Field Engineer-John Peter S | Problem solved-Field Operations Manager-Devasudar Singh | closed-Phone Technical Support-Senthil M. | RCA will be done based on failure rate-Functionality Support Lead-Shankar Anand R. | -Quality-Vijay Chinnaswamy	IMG_20160315_093215.jpg AI module | IMG_20160315_093353.jpg RV8 Valve | IMG_20160315_093323.jpg pressure transducer
CIR-10000361	100260110	Amarjothi Spinning Mills Limited	Theni-Kadamalaigundu	WF-IN-022-0846-Y3-A-001	0.85	65	Standard	Indar	20305001154	Gamesa(China)	601993	High Temperature	STD+	Standard	13/06/2010	402348799	29/04/2016	-0	Dinesh Babu R.	1404	1440	30/04/2016 15:00:00	29/04/2016 09:00:00	8468520	42845	MECHANICAL	BLADES			LIGHTNING		Blade 'A', 'B', 'C' diverter strip replaced work down.	Diverter strip damage		SF.NO:282(AMARJOTHI)	Lightening	5000930, 5006550, 5006555(S.Sunder, Raja, Rajesh,Venkatesh)	Diverter strip replaced by new one.		Lightening	Assigned	Blade 'A', 'B', 'C' diverter strip replaced work down.	Blade 'A', 'B', 'C' diverter strip replaced work down.-Field Engineer-Dinesh Babu R. | Blade repair work done-Field Operations Manager-Devasudar Singh | Lightning conductor connectivity must ensured-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.
CIR-10000069	100260117	Bannari Amman Flour Mill Limited	Theni-Kadamalaigundu	WF-IN-022-0846-Y2-A-002	0.85	65	Standard	Indar	20305001175	Gamesa(China)	602053	High Temperature	STD+	Standard	03/07/2010	402282696	29/02/2016	-0	Senthil Kannan G	1404	1425	29/02/2016 12:30:37	29/02/2016 10:00:37	8236930	41104	CONTROL SYSTEM	NACELLE INSTRUMENTATION SYSTEM	GP005426, GP021828	PHONIEX, YUASA	NORMAL OPERATION		Wtg Manually stopped due to warning error no:707 SMP Communication failure. We checked & found top side SMP box failure & also Battery back up 12V battery failure.	SMP box & 12Vbattery back up battery failure.	Breakdown	SF.NO:275(BANNARI AMMAN)	Grid Fluctuation, Short circuit, Over voltage, Earth fault, Material problem	G.Senthilkannan	SMP BOX & 12V Battery replaced.	01no, 02no's	Grid Fluctuation, Short circuit, Over voltage, Earth fault, Material problem	Assigned	We checked & found top side SMP box failure & also Battery back up 12V battery failure. We replaced all & start the WTG	Wtg Manually stopped due to warning error no:707 SMP Communication failure. We checked & found top side SMP box failure & also Battery back up 12V battery failure. We replaced all & start the WTG. -Field Engineer-Senthil Kannan G | Problem solved-Field Operations Manager-Devasudar Singh | to be investigated-Phone Technical Support-Senthil M. | SMP board failure mode analysis required-Functionality Support Lead-Murugesan P. | FMEA required-Functionality Support Specialist-Venkatesh S | -Quality-Vijay Chinnaswamy	IMG_20160301_154916.jpg SMP | Battery 12V.jpg 12V Battery
CIR-10000098	100260117	Bannari Amman Flour Mill Limited	Theni-Kadamalaigundu	WF-IN-022-0846-Y2-A-002	0.85	65	Standard	Indar	20305001175	Gamesa(China)	602053	High Temperature	STD+	Standard	03/07/2010	402298243	10/03/2016	-0	Devasudar Singh	1404	1425	10/03/2016 12:30:00	10/03/2016 11:00:00	8241930	41320	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	50071	INGETEAM	NORMAL OPERATION	4176115650	Wtg stopped due to error no:2231 Error in phase 'T' inverter . we check & found Inverter side drivercard failure.	Driver card problem	Breakdown	SF.NO:275(BANNARIAMMAN)	Material problem, Grid fluctuation	K.Sankaranarayanan, S.Johnpeter, T.Stalinkumar	Inverter section driver card changed by new one.	01no	Material problem, Grid fluctuation, Short circuit	Assigned	We check & found inverter section driver card failure. so we replaced new one.	Wtg stopped due to error no:2231 Error in phase 'T' inverter . we check & found Inverter side drivercard failure. So we changed by new one.-Field Engineer-John Peter S | Problem solved-Field Operations Manager-Devasudar Singh | DURING SURGE-Phone Technical Support-Senthil M. | There is some driver card DM available in the SB and we have to check and apply the same-Functionality Support Lead-Murugesan P. | its being already in implementation-Functionality Support Specialist-Venkatesh S | -Quality-Vijay Chinnaswamy	IMG_20160310_210412.jpg Driver card
CIR-10000096	100260119	JPP Mills (P) Ltd	Theni-Kadamalaigundu	WF-IN-022-0846-Y2-A-006	0.85	65	Standard	Indar	20305001163	Gamesa(China)	602023	High Temperature	STD+	Standard	20/08/2010		07/03/2016	-0	Sankaranarayanan K	1404	1425	07/03/2016 16:15:18	07/03/2016 14:30:18	6836820	39772	ELECTRICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	880162	VICKERS	NORMAL OPERATION	G52-C-1993	WTG stopped due to error no:800 Pitch Activating error	Proportional valve problem	Breakdown	SF.NO:333(JPP2)	Frequent operation, Material Defect	K.Sankaranarayanan, M.Avudaiappan	Proportional valve changed by new one.	01no	Frequent operation, Material Defect	Assigned	We check & found Proportional Valve Problem	WTG stopped due to error no:800 Pitch Activating error. We check & found Proportional Valve Problem . so we changed by new one. -Field Engineer-Sankaranarayanan K | problem solved-Field Operations Manager-Devasudar Singh | Kindly Check if any DM is available to control the Proportional valve failure-Phone Technical Support-Senthil M. | Site - To check if the DM - B5041203-EN_R00 is implemented. More details about SB, please contact PTS India-Functionality Support Lead-Anand A.P | -Quality-Vijay Chinnaswamy	IMG_20160308_190017.jpg Pro.Valve
CIR-10000061	100260158	Sri Iyyan Textile Mills (P) Ltd	Theni-Kadamalaigundu	WF-IN-022-0846-Y2-A-005	0.85	65	Standard	Indar	20305001179	Gamesa(China)	602109	High Temperature	STD+	Standard	13/08/2010	402276177	22/02/2016	-0	Dinesh Babu R.	1404	1425	22/02/2016 17:30:51	22/02/2016 16:30:51	7455270	40043	MECHANICAL	GENERATOR SYSTEM	50591,50592,P393462	GAMESA, ABB	NORMAL OPERATION		WTG Manual stopped for 60Month service work. We check & found phase carbon brush 06noâ€™s , Ground carbon brush 01no warn out & Hydraulic contactor failure.	Phase & Ground Carbon brush & Hyd.contactor.	During service time	SF.NO:278(SRI IYYAN)	Frequent operation, Material Defect	R.Dineshbabu, K.Sankar,M.Vinu	Carbon brush & Hyd.contactor changed by new one.	06no's, 01no,01no	Frequent operation, Material Defect	Assigned	We check & found phase carbon brush 06noâ€™s , Ground carbon brush 01no warn out & Hydraulic contactor failure. We replaced all and start the WTG.	WTG Manual stopped for 60Month service work. We check & found phase carbon brush 06noâ€™s , Ground carbon brush 01no warn out & Hydraulic contactor failure. We replaced all and start the WTG -Field Engineer-Dinesh Babu R. | Problem solved-Field Operations Manager-Devasudar Singh | consumables-Phone Technical Support-Senthil M. | frequency of carbon brush replacement to be ensured-Functionality Support Lead-Murugesan P. | -Quality-Vijay Chinnaswamy	IMG_20160202_164656_HDR.jpg Hyd.contactor | Carbon brush.jpg
CIR-10000044	100260089	JPP Mills (P) Ltd	Theni-Kadamalaigundu	WF-IN-022-0846-Y2-A-007	0.85	65	Standard	Indar	20305000884	Gamesa(China)	601916	High Temperature	STD+	Standard	02/07/2010		17/02/2016	-0	Avudaippan M	1404	1425	17/02/2016 15:30:14	17/02/2016 13:00:14	7572390	40609	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP019507, P393180	FINDER	GRID FAILURE		Wtg stopped due to error no:2212 Grid voltage failure. We Check & found 1000Amps fuse & Bottom (ODT) On delay timer was failure.								Frequent operation,Material problem Short circuit, Loose connection.	Assigned	We Check & found 1000Amps fuse & Bottom (ODT) On delay timer was failure. We replaced by new one and restarted the turbine.	Wtg stopped due to error no:2212 Grid voltage failure. We Check & found 1000Amps fuse & Bottom (ODT) On delay timer was failure. We replaced by new one and restarted the turbine. -Field Engineer-Avudaippan M | Problem Solved-Field Operations Manager-Devasudar Singh | BOP Auditing to be done-Phone Technical Support-Senthil M. | BOP audit required-Functionality Support Lead-Murugesan P. | -Quality-Vijay Chinnaswamy	IMG_20160220_164408.jpg
CIR-10000109	100260089	JPP Mills (P) Ltd	Theni-Kadamalaigundu	WF-IN-022-0846-Y2-A-007	0.85	65	Standard	Indar	20305000884	Gamesa(China)	601916	High Temperature	STD+	Standard	02/07/2010		16/03/2016	-0	Balasubramanian G.	1404	1440	16/03/2016 15:40:00	16/03/2016 14:30:00	7584100	41199	ELECTRICAL	NACELLE INSTRUMENTATION SYSTEM	GP004262, P393462	PHONIEX, ABB	NORMAL OPERATION		WTG Stopped due to error no:208 Hu.Activation failure. nd step: We Checked and found KR280 PLC relay & KM280 contactor was failure	PLC 24V relay, Hyd.contactor failure.	Breakdown	Sf.no:315(JPP1)	Continuos(on and off) operating, Grid Fluctuation. Grid down for long time and Fluctuation.	G.Balasubramanian, D.Yukesh	PLC 24V relay, Hyd.contactor replaced	each 01no	Continuos(on and off) operating, Grid Fluctuation. Grid down for long time and Fluctuation.	Assigned	We Checked and found KR280 PLC relay & KM280 contactor was failure. We replaced KR280 relay & KM280 contactor and restart the turbine	WTG Stopped due to error no:208 Hu.Activation failure. We Checked and found KR280 PLC relay & KM280 contactor was failure. We replaced KR280 relay & KM280 contactor and restart the turbine-Field Engineer-Balasubramanian G. | problem solved-Field Operations Manager-Devasudar Singh | solved , DM Implementation to be ensured-Phone Technical Support-Senthil M. | As per field alert contactor replacement to be checked once in 4 years-Functionality Support Lead-Murugesan P. | -Quality-Vijay Chinnaswamy	IMG_20151024_220559.jpg Hyd.Contactor | IMG_20160202_164656_HDR.jpg Hyd.Contactor | IMG_20160302_130116.jpg PLC RELAY
CIR-10000115	100260089	JPP Mills (P) Ltd	Theni-Kadamalaigundu	WF-IN-022-0846-Y2-A-007	0.85	65	Standard	Indar	20305000884	Gamesa(China)	601916	High Temperature	STD+	Standard	02/07/2010		16/03/2016	-0	Devasudar Singh	1404	1440	16/03/2016 15:40:00	16/03/2016 14:30:00	7584100	41199	ELECTRICAL	NACELLE INSTRUMENTATION SYSTEM	GP004262, P393462	PHONIEX, ABB	NORMAL OPERATION
CIR-10000128	100260082	Alvittas Electricals (P) Ltd	Theni-Alagapuri	WF-IN-022-0834-Y2-A-005	0.85	65	Standard	Indar	20305001112	Gamesa(China)	601925	High Temperature	STD+	Standard	20/08/2010	402305922	17/03/2016	-0	Devasudar Singh	1404	1440	17/03/2016 23:00:00	17/03/2016 21:00:00	7993310	40522	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004895, GP005798	PHONIEX, GAMESA	NORMAL OPERATION	1113626909										Deleted
CIR-10000260	100260193	K.R.Nagarajan	Theni-Alagapuri	WF-IN-022-0834-Y1-A-003	0.85	65	Standard	Indar	20305001245	Gamesa(Spain)	300045	High Temperature	STD+	Standard	17/09/2010	402322243	02/04/2016	210-Brake drive error	Devasudar Singh	1404	1440	02/04/2016 17:30:00	02/04/2016 17:00:00	8518940	40186	MECHANICAL	GENERATOR SYSTEM	50591,50592	GAMESA	NORMAL OPERATION		During service time we check & found Phase carbon brush, Ground carbon brush warn out.	Phase carbon brush, groundcarbon brush warnout	during service time	SF.NO:53(RAMRAJ)	Material defect, continuous operation	R.Dineshbabu, G.Senthilkannan, A.Parasuraman	we replaced 09no's Phase carbon brush, 01no groundcarbon brush by new.	09no's, 01no	Material defect, continuous operation.		We replaced new carbon brush
CIR-10000094	100260193	K.R.Nagarajan	Theni-Alagapuri	WF-IN-022-0834-Y1-A-003	0.85	65	Standard	Indar	20305001245	Gamesa(Spain)	300045	High Temperature	STD+	Standard	17/09/2010	402286974	02/03/2016	216-High number of start-ups in hydr unit	Devasudar Singh	1404	1425	03/02/2016 12:00:40	03/02/2016 10:00:40	8511710	39510	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	GP004893	OLEAR	NORMAL OPERATION
CIR-10000151	100260193	K.R.Nagarajan	Theni-Alagapuri	WF-IN-022-0834-Y1-A-003	0.85	65	Standard	Indar	20305001245	Gamesa(Spain)	300045	High Temperature	STD+	Standard	17/09/2010	402307776	18/03/2016	-0	Devasudar Singh	1404	1440	18/03/2016 12:45:00	18/03/2016 11:30:00	8515510	39860	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP019518	MOXA	NORMAL OPERATION		Wtg manually stopped for error no:707 SMP communication failure, so we check & found MOXA failure	MOXA failure	Checking time	SF.NO:53(RAMRAJ)	Continuous operation, due to heat,grid drop	G.Senthilkannan, A.Parasuraman	Moxa replaced	01no	Grid drop, Continuous operation, due to heat	Closed	Moxa replaced by new one	Problem solved-Field Operations Manager-Devasudar Singh | solved-Phone Technical Support-Senthil M. | MOXA failure Analysis to be done-Functionality Support Lead-Shankar Anand R. | not in top 10 failure. will be opened if repeat cases-Quality-Vijay Chinnaswamy
CIR-10000092	100260133	K.P.R. Mill Ltd	Theni-Alagapuri	WF-IN-022-0834-Y1-A-015	0.85	65	Standard	Indar	20305001195	Gamesa(China)	602079	High Temperature	STD+	Standard	20/08/2010	402285579	01/03/2016	-0	Devasudar Singh	1404	1425	03/01/2016 07:00:16	03/01/2016 04:50:16	8090070	40162	CONTROL SYSTEM	NACELLE INSTRUMENTATION SYSTEM	GP004262	PHONIEX	NORMAL OPERATION											Deleted
CIR-10000150	100260118	Chenduran Cotspin (India) Pvt. Ltd	Theni-Alagapuri	WF-IN-022-0834-Y1-A-007	0.85	65	Standard	Indar	20305001174	Gamesa(China)	602054	High Temperature	STD+	Standard	18/08/2010	402307773	18/03/2016	-0	Devasudar Singh	1404	1440	18/03/2016 11:15:00	18/03/2016 10:00:00	9131470	40449	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP019518	MOXA	NORMAL OPERATION											Deleted
CIR-10000363	100260120	Amarjothi Spinning Mills Limited	Theni-Alagapuri	WF-IN-022-0834-Y1-A-006	0.85	65	Standard	Indar	20305001170	Gamesa(China)	602058	High Temperature	STD+	Standard	23/08/2010	402353351	04/05/2016	-0	Devasudar Singh	1404	1440	05/05/2016 15:00:00	04/05/2016 09:00:00	8892840	41533	MECHANICAL	BLADES			LIGHTNING		Blade 'A', 'B', 'C' diverter strip fixing work down.	Diverter strip problem		SF.NO:123(AMARJOTHI)	Lightening	5000930, 5006550, 5006555, 5003613(S.Sunder, Raja, Rajesh,Venkatesh, T.Stalinkumar)	Diverter strip replaced		Lightening	Assigned	Blade 'A', 'B', 'C' diverter strip fixing work down.	Blade 'A', 'B', 'C' diverter strip fixing work down.-Field Engineer-Dinesh Babu R. | Blade repair work completed-Field Operations Manager-Devasudar Singh | Blade Lightning conductor connectivity must ensured-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.
CIR-10000330	100260089	JPP Mills (P) Ltd	Theni-Kadamalaigundu	WF-IN-022-0846-Y2-A-007	0.85	65	Standard	Indar	20305000884	Gamesa(China)	601916	High Temperature	STD+	Standard	02/07/2010	402344479	26/04/2016	205-Low oil level in hydraulic unit	Devasudar Singh	1404	1440	26/04/2016 18:00:00	26/04/2016 16:00:00	7601510	42172	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	GP004893	OLEAR	NORMAL OPERATION		Wtg stopped due to error no:205 Low Hu.cooling oil. we check & found Pitch accmulator failure.	Pitch accmulator failure	Breakdown	SF.NO:315(JPP1)	Continuous operation, grid drop frequently	S.Johnpeter, K.Sankaranarayanan	we replaced new pitch accmulator	01no	Continuous operation, grid drop frequently	Assigned	we replaced by new pitch accmulator.	Wtg stopped due to error no:205 Low Hu.cooling oil. we check & found Pitch accmulator failure.so we replaced by new one.-Field Engineer-John Peter S | Problem solved-Field Operations Manager-Devasudar Singh | N2 pre charge pressure must ensured during Maintenance-Phone Technical Support-Senthil M. | Issue Closed. Deva: Please ensure to check the Pre charge pressure during PM-Functionality Support Lead-Anand A.P | -Quality-Vijay Chinnaswamy	IMG_20160303_164134.jpg Pitch accmulator
CIR-10000547	100260089	JPP Mills (P) Ltd	Theni-Kadamalaigundu	WF-IN-022-0846-Y2-A-007	0.85	65	Standard	Indar	20305000884	Gamesa(China)	601916	High Temperature	STD+	Standard	02/07/2010	402374595	26/05/2016	-0	Senthil Kannan G	1404	1440	26/05/2016 04:30:00	26/05/2016 00:30:00	7649550	42742	MECHANICAL	BLADE BEARING SYSTEM	P630694	DYSTA	NORMAL OPERATION		WTG Manually stopped for blade hub joint broken bolt replacement work. We replaced M24X180 broken bolt 5 noâ€™s replaced it(Blade no:A ,POS 3,4,5,6,7)	Blade bearing bolt broken	during visual inspection time	SF.NO:315(JPP)	Material defect ,wrong thread Quality issue, exceeded to torque limit	G.Senthilkannan, S.Johnpeter	We replaced broken bolts by new one.	14no's	Material defect ,wrong thread. Quality issue, exceeded to torque limit	Assigned	We replaced M24X180 broken bolt 5 noâ€™s replaced it(Blade no:A ,POS 3,4,5,6,7). We installed new bolt and restarted it WTG.	WTG Manually stopped for blade hub joint broken bolt replacement work. We replaced M24X180 broken bolt 5 noâ€™s replaced it(Blade no:A ,POS 3,4,5,6,7) . We installed new bolt and restarted it WTG.-Field Engineer-Senthil Kannan G | Problem solved-Field Operations Manager-Devasudar Singh | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Anand A.P	Blade bearing bolt.jpg Blade bearing bolt
CIR-10000060	100260090	Rajashree Spintex Pvt. Ltd.	Theni-Kadamalaigundu	WF-IN-022-0846-Y2-A-004	0.85	65	Standard	Indar	20305001149	Gamesa(China)	601936	High Temperature	STD+	Standard	22/05/2010	402274272	21/02/2016	-0	John Peter S	1404	1425	21/02/2016 16:30:56	21/02/2016 14:30:56	8444760	41224	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	109537		NORMAL OPERATION		Wtg stopped due to error no:2114 Analog card failure. We checked & Found yaw manifold pressure transducer failure.	Pressure transducer failure	breakdown	SF.NO:224(RAJASHREE)	Grid Fluctuation,Material defective,Input voltage problem, Continuous operation,	M.Vinumonikandan, S.Johnpeter	Pressure transducer	01no	Grid Fluctuation,Material defective,Input voltage problem, Continuous operation,	Assigned	We checked & Found yaw manifold pressure transducer failure We replaced by new one and rastart the turbine.	Wtg stopped due to error no:2114 Analog card failure. We checked & Found yaw manifold pressure transducer failure We replaced by new one and rastart the turbine. -Field Engineer-John Peter S | Closed-Field Operations Manager-Devasudar Singh | Component level RCA recommanded-Phone Technical Support-Senthil M. | RCA to be carried out based on failure rate-Functionality Support Lead-Shankar Anand R. | -Quality-Vijay Chinnaswamy
CIR-10000056	100260080	S Basanth	Theni-Gandamanur	WF-IN-022-0846-Y1-A-001	0.85	65	Standard	Indar	20305001123	Gamesa(China)	601935	High Temperature	STD+	Standard	13/04/2010		19/02/2016	-0	Avudaippan M	1404	1425	19/02/2016 14:40:58	19/02/2016 13:40:58	9945390	43188	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP188019	SAFETEC	NORMAL OPERATION		Wtg stopped due to error no:2212 Grid voltage failure. We check & found F51 Surgr arrestor was failed.								Grid fluctuation, Grid drop,due to earth fault.	Assigned	check & found F51 Surgr arrestor was failed. We replaced surge arrestor then restart the turbine.	Wtg stopped due to error no:2212 Grid voltage failure. check & found F51 Surgr arrestor was failed. We replaced surge arrestor then restart the turbine. -Field Engineer-Avudaippan M | Problem Solved-Field Operations Manager-Devasudar Singh | BOP Audit to be done-Phone Technical Support-Senthil M. | Type I surge arrester sent to Theni WF for further validation-Functionality Support Lead-Murugesan P. | Component failure due to grid voltage failure-Functionality Support Specialist-Mayank | -Quality-Vijay Chinnaswamy
CIR-10000321	100260080	S Basanth	Theni-Gandamanur	WF-IN-022-0846-Y1-A-001	0.85	65	Standard	Indar	20305001123	Gamesa(China)	601935	High Temperature	STD+	Standard	13/04/2010	402343191	25/04/2016	205-Low oil level in hydraulic unit	Devasudar Singh	1404	1439	25/04/2016 01:05:00	25/04/2016 00:05:00	9991660	44672	ELECTRICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	109090		NORMAL OPERATION		Wtg stopped due to error no:205 Hydraulic oil level low. we check & found hyd.oil level sensor was failure.	Hyd.oil level Indicator failure	Breakdown	SF.NO:299(BASANTH)	Continuous operation, material defect	M.Vinumonikanndan	we replaced new hyd.oil level indicator.	01no	Continuous operation, material defect	Assigned	We replaced new oil level sensor	Wtg stopped due to error no:205 Hydraulic oil level low. we check & found hyd.oil level sensor was failure.we replaced by new one.-Field Engineer-Vinu Monikandan | Problem solved-Field Operations Manager-Devasudar Singh | Further investigation recommended-Phone Technical Support-Senthil M. | Issue closed. Low cost material-Functionality Support Lead-Anand A.P | -Quality-Vijay Chinnaswamy	IMG_20160425_095139.jpg
CIR-10000127	100260082	Alvittas Electricals (P) Ltd	Theni-Alagapuri	WF-IN-022-0834-Y2-A-005	0.85	65	Standard	Indar	20305001112	Gamesa(China)	601925	High Temperature	STD+	Standard	20/08/2010	402305922	17/03/2016	-0	Stalin Kumar T	1404	1440	17/03/2016 23:00:00	17/03/2016 21:00:00	7993310	40522	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004895, GP005798	PHONIEX, GAMESA	NORMAL OPERATION	1113626909	Wtg stopped due to error no:2118 Interbus error & 411 High brake temp. we check & found RTD module failure & also Brake thermistor open.	RTD module, Brake pad with thermistor open	Breakdown	SF.NO:382(ALVITAS)	Continuous operation, due to heat	T.Stalinkumar, S.Johnpeter	RTD module, Brake pad with thermistor open so changed by new one.	each 01no	Continuous operation , Grid drop, due to heat	Assigned	We check & found RTD module failure & Brake thermistor open, so changed by new one.	Wtg stopped due to error no:2118 Interbus error & 411 High brake temp. we check & found RTD module failure & also Brake thermistor open.So we replaced all by new one.-Field Engineer-Stalin Kumar T | Problem solved-Field Operations Manager-Devasudar Singh | solved-Phone Technical Support-Senthil M. | RCA will be done based on failure rate-Functionality Support Lead-Shankar Anand R. | -Quality-Vijay Chinnaswamy	IMG_20160302_130152.jpg RTD | Brake pad.jpg
CIR-10000043	100260086	Green Infra Limited	Theni-Alagapuri	WF-IN-022-0834-Y1-A-013	0.85	65	Standard	Indar	20305001150	Gamesa(China)	601950	High Temperature	STD+	Standard	17/08/2010	402269557	16/02/2016	-0	Avudaippan M	1404	1425	16/02/2016 14:00:26	16/02/2016 12:00:26	8609900	39860	CONTROL SYSTEM	NACELLE INSTRUMENTATION SYSTEM	GP004262, P393462	PHONIEX, ABB	NORMAL OPERATION		Wtg stopped due to error no:208 HU.Activation failure.								Continuos(on and off) operating, Grid Fluctuation	Assigned	Hydraulic PLC relay(24V) & Contactor (A26-30-10) Changed.	WTG Stopped due to error no:208 HU Activation failure. We Checked and found KR280 PLC relay & KM280 contactor was failure We replaced KR280 relay & KM280 contactor and restart the turbine -Field Engineer-Avudaippan M | Problem Solved-Field Operations Manager-Devasudar Singh | DM Solution recommended-Phone Technical Support-Senthil M. | Once in 4years contator replacement is recommended-Functionality Support Lead-Murugesan P. | -Quality-Vijay Chinnaswamy
CIR-10000066	100260086	Green Infra Limited	Theni-Alagapuri	WF-IN-022-0834-Y1-A-013	0.85	65	Standard	Indar	20305001150	Gamesa(China)	601950	High Temperature	STD+	Standard	17/08/2010	402282693	28/02/2016	-0	Senthil Kannan G	1404	1425	28/02/2016 12:00:37	28/02/2016 10:00:37	8619430	40081	CONTROL SYSTEM	NACELLE INSTRUMENTATION SYSTEM	GP005426	PHONIEX	NORMAL OPERATION		Wtg Manually stopped due to warning error no:707 SMP Communication failure. We checked & found top side SMP box failure.	SMP Failure	Breakdown	SF.NO:09(GREEN INFRA)	Grid Fluctuation, Short circuit, Over voltage, Earth fault, Material problem	S.Johnpeter, G.senthilkannan	SMP BOX replaced	01no	Grid Fluctuation, Short circuit, Over voltage, Earth fault, Material problem	Assigned	We checked & found top side SMP box failure. We replaced the SMP & start the WTG	Wtg Manually stopped due to warning error no:707 SMP Communication failure. We checked & found top side SMP box failure. We replaced the SMP & start the WTG. -Field Engineer-Senthil Kannan G | Problem solved-Field Operations Manager-Devasudar Singh | to be investigated-Phone Technical Support-Senthil M. | Please send the failure SMP to chennai office for repair and collect the data from new Installed SMP to check the proper configuration-Functionality Support Lead-Hemkumar D | -Quality-Vijay Chinnaswamy
CIR-10000310	100260086	Green Infra Limited	Theni-Alagapuri	WF-IN-022-0834-Y1-A-013	0.85	65	Standard	Indar	20305001150	Gamesa(China)	601950	High Temperature	STD+	Standard	17/08/2010	402338824	20/04/2016	210-Brake drive error	Devasudar Singh	1404	1440	20/04/2016 17:30:00	20/04/2016 16:00:00	8650860	41245	MECHANICAL	NACELLE INSTRUMENTATION SYSTEM	109882, GP004262, GP005002	OLEAR, PHONIEX, ABB	NORMAL OPERATION		During service time error no:210 Brake drive error occur, that time we check & found brake accmulator failure,KR173 relay also failure .	Brake accmulator, 24VPLC relay failure	During service time	SF.NO:09(Green infra)	Continuuous operation, Material defect	G.Senthilkannan, G.Balasubramanian,D.Yukesh	Brake accmulator, 24VPLC relay replaced by new one.	Each 01no	Continuuous operation, Material defect	Closed	We replaced brake accmulator, PLC relay	During service time error no:210 Brake drive error occur, that time we check & found brake accmulator failure,KR173 relay also failure .So we replaced all by new one.-Field Engineer-Senthil Kannan G | Problem solved-Field Operations Manager-Devasudar Singh | Accumulator pre charge pressure during service must be ensured-Phone Technical Support-Senthil M. | Issue closed.-Functionality Support Lead-Anand A.P | kr 173 relay to be anlaysed by repair ciruit-Quality-Vijay Chinnaswamy	IMG_20160302_130624.jpg Brake accmulator | IMG_20160302_130116.jpg PLC Relay
CIR-10000323	100260088	Green Infra Limited	Theni-Alagapuri	WF-IN-022-0834-Y1-A-016	0.85	65	Standard	Indar	20305001151	Gamesa(China)	601944	High Temperature	STD+	Standard	19/08/2010	402343203	25/04/2016	411-High brake temperature	Devasudar Singh	1404	1440	25/04/2016 17:30:00	25/04/2016 16:00:00	8387470	41386	MECHANICAL	NACELLE INSTRUMENTATION SYSTEM	P370104, P393462, 50591,50592	GAMESA, ABB	NORMAL OPERATION		During service time we check & found normal brake pad warnout & hyd.contactor failure, Phase carbon brush, Ground carbon brush warnout.	Normal brake pad, Phase & Ground carbon brush warnout,hyd.contactor failure	during service time.	SF.NO:985(GREEN INFRA)	Continuous operation, material defect	S.Johnpeter, D.Yukesh, G.Bala	Normal brake pad, Phase & Ground carbon brush warnout,hyd.contactor replaced by new one.	03no's,12no's, 01no,01no	Continuous operation, material defect	Assigned	we replaced all by new one.	During service time we check & found normal brake pad warnout & hyd.contactor failure, Phase carbon brush, Ground carbon brush warnout.we replaced all by new one.-Field Engineer-Balasubramanian G. | problem solved-Field Operations Manager-Devasudar Singh | CIR not required for these Items-Phone Technical Support-Senthil M. | closed-Functionality Support Lead-Murugesan P. | -Quality-Vijay Chinnaswamy	Brake pad.jpg Brake pad | Carbon brush.jpg Carbon brush | IMG_20160202_164656_HDR.jpg Hyd.contactor
CIR-10000600	100260109	Shiny Knitwear (P) Ltd.	Theni-Alagapuri	WF-IN-022-0834-Y2-A-009	0.85	65	Standard	Indar	20305001158	Gamesa(China)	602009	High Temperature	STD+	Standard	22/09/2010	402390169	07/06/2016	-0	Devasudar Singh	1404	1440	07/06/2016 13:00:00	07/06/2016 09:30:00	7788770	41464	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP012531, 50071	EUPEC, INGITEAM	NORMAL OPERATION	5070917287	Wtg stopped due to error no.2230 Error in â€˜Sâ€™ Phase Inverter We checked and found inverter Section 3 Phase of IGBTâ€™s and driver card was failure	IGBT's & driver card failure	breakdown	SF.NO:641(Shiny)	Material problem, Grid fluctuation Short circuit,	K.Sanakaranarayanan, M.Avudaiappan, M.Gopi	We replaced IGBT & driver card	06no's, 01no	Material problem, Grid fluctuation Short circuit,	Assigned	We checked and found inverter Section 3 Phase of IGBTâ€™s and driver card was failure. We replaced by new one and start the turbine	: Wtg stopped due to error no.2230 Error in â€˜Sâ€™ Phase Inverter. We checked and found inverter Section 3 Phase of IGBTâ€™s and driver card was failure.We replaced by new one and start the turbine-Field Engineer-Sankaranarayanan K | Problem solved-Field Operations Manager-Devasudar Singh | FSL comments requested-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.	IGBT EUPEC.jpg IGBT | IMG_20160609_102843.jpg Drivercard
CIR-10000093	100260193	K.R.Nagarajan	Theni-Alagapuri	WF-IN-022-0834-Y1-A-003	0.85	65	Standard	Indar	20305001245	Gamesa(Spain)	300045	High Temperature	STD+	Standard	17/09/2010		02/03/2016	-0	John Peter S	1404	1425	02/03/2016 12:00:40	02/03/2016 10:00:40	8511710	39510	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	GP004893	OLEAR	NORMAL OPERATION		Wtg stopped due to error no:216 Hign no.of starts GH. we check & found pitch accmulator failure.	Pitch accmulator failure	Breakdown	SF.NO:53(RAMRAJ)	Continuous operation, frequently grid drop. Hyd.Motor Continuous ON OFF condition	S.Johnpeter, A.Parasuraman	Pitch accmulator replaced	01no	Continuous operation, frequently grid drop. Hyd.Motor Continuous ON OFF condition	Assigned	We check & found pitch accmullator failure, so we replaced by new one.	Wtg stopped due to error no:216 Hign no.of starts GH. we check & found pitch accmulator failure. so we replaced pitch accmulator & restart the turbine.-Field Engineer-John Peter S | problem solved-Field Operations Manager-Devasudar Singh | Scheduled service Auditing to be tighten-Phone Technical Support-Senthil M. | Please send the failure accumulator to repair circuit for RCA-Functionality Support Lead-Anand A.P | -Quality-Vijay Chinnaswamy	IMG_20160303_164134.jpg Pitch accmulator
CIR-10000373	100260120	Amarjothi Spinning Mills Limited	Theni-Alagapuri	WF-IN-022-0834-Y1-A-006	0.85	65	Standard	Indar	20305001170	Gamesa(China)	602058	High Temperature	STD+	Standard	23/08/2010	402356530	07/05/2016	-0	Kalimuthu J	1404	1440	07/05/2016 16:30:00	07/05/2016 13:00:00	8893620	41596	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP013311	INGETEAM	LIGHTNING	435964457	Wtg stopped due to error no 2208 Emergency series Notok. we check & found crowbar card failure.	Crowbar card failure	breakdown	SF.NO:123(AMARJOTHI)	Heavy lightening	K.Ramesh, J.Kalimuthu, T.Stalinkumar	we replaced new crowbar card	01no	Heavy lightening	Assigned	we replaced crowbar card by new one.	Wtg stopped due to error no 2208 Emergency series Notok. we check & found crowbar card failure.we replaced by new one.-Field Engineer-Kalimuthu J | Problem solved-Field Operations Manager-Devasudar Singh | Lightning-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.	IMG_20160509_230123.jpg Crowbar card
CIR-10000362	100260114	Amarjothi Spinning Mills Limited	Theni-Alagapuri	WF-IN-022-0834-Y2-A-001	0.85	65	Standard	Indar	20305001166	Gamesa(China)	602028	High Temperature	STD+	Standard	21/08/2010	402350302	02/05/2016	-0	Dinesh Babu R.	1404	1440	03/05/2016 13:00:00	02/05/2016 09:00:00	8492910	41481	MECHANICAL	BLADES			LIGHTNING		Blade 'A', 'B', 'C' diverter strip replaced work down.	Diverter strip damage		SF.NO:83(AMARJOTHI)	Lightening	5000930, 5006550, 5006555(S.Sunder, Raja, Rajesh,Venkatesh)	Diverter strip replaced by new one.		Lightening	Assigned	Blade 'A', 'B', 'C' diverter strip replaced work down.	Blade 'A', 'B', 'C' diverter strip replaced work down.-Field Engineer-Dinesh Babu R. | Blade repair work done-Field Operations Manager-Devasudar Singh | Lightning discharge conductor connectivity must ensured-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.
CIR-10000218	100260106	Green Infra Limited	Theni-Alagapuri	WF-IN-022-0834-Y2-A-004	0.85	65	Standard	Indar	20305001159	Gamesa(China)	601985	High Temperature	STD+	Standard	19/08/2010	402313662	25/03/2016	-0	Devasudar Singh	1404	1440	25/03/2016 14:00:00	25/03/2016 12:00:00	8148990	40679	ELECTRICAL	NACELLE INSTRUMENTATION SYSTEM	GP005455		NORMAL OPERATION
CIR-10000350	100260431	KHATAU NARBHERAM & CO	Theni-Srirangapuram	WF-IN-022-0835-Y3-A-018	0.85	65	Standard	Gamesa wind Tianjin, China	801001161	Gamesa(China)	602466	High Temperature	STD+	Standard	27/09/2011	402338821	18/04/2016	-0	Sundaresa Perumal S.	1404	1439	20/04/2016 18:00:00	18/04/2016 09:00:00	6209670	31658	MECHANICAL	BLADES			NORMAL OPERATION		Blade A,B,C Diverter strip replaced & Blade B Tip repair work done.								Due to lightening damage		Blade A,B,C Diverter strip replaced & Blade B Tip repair work done.
CIR-10000120	100260193	K.R.Nagarajan	Theni-Alagapuri	WF-IN-022-0834-Y1-A-003	0.85	65	Standard	Indar	20305001245	Gamesa(Spain)	300045	High Temperature	STD+	Standard	17/09/2010		18/03/2016	-0	Senthil Kannan G	1404	1440	18/03/2016 12:45:00	18/03/2016 11:30:00	8515510	39860	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP019518	MOXA	NORMAL OPERATION		Wtg manually stopped for error no:707 SMP communication failure, so we check & found MOXA failure	MOXA failure	Checking time	SF.NO:53(RAMRAJ)	Continuous operation, due to heat,grid drop	G.Senthilkannan, A.Parasuraman	Moxa replaced	01no	Grid drop, Continuous operation, due to heat	Assigned	We check & found moxa failure. so we replaced by new one, now machine running normal.	Wtg manually stopped for error no:707 SMP communication failure, so we check & found MOXA failure. we replaced by new one.-Field Engineer-Senthil Kannan G | Problem solved-Field Operations Manager-Devasudar Singh | solved-Phone Technical Support-Senthil M. | RCA to be done based on failure rate-Functionality Support Lead-Shankar Anand R. | -Quality-Vijay Chinnaswamy	IMG_20160318_183353.jpg MOXA
CIR-10000235	100260193	K.R.Nagarajan	Theni-Alagapuri	WF-IN-022-0834-Y1-A-003	0.85	65	Standard	Indar	20305001245	Gamesa(Spain)	300045	High Temperature	STD+	Standard	17/09/2010		02/04/2016	210-Brake drive error	Dinesh Babu R.	1404	1440	02/04/2016 17:30:00	02/04/2016 17:00:00	8518940	40186	MECHANICAL	GENERATOR SYSTEM	50591,50592	GAMESA	NORMAL OPERATION		During service time we check & found Phase carbon brush, Ground carbon brush warn out.	Phase carbon brush, groundcarbon brush warnout	during service time	SF.NO:53(RAMRAJ)	Material defect, continuous operation	R.Dineshbabu, G.Senthilkannan, A.Parasuraman	we replaced 09no's Phase carbon brush, 01no groundcarbon brush by new.	09no's, 01no	Material defect, continuous operation.	Assigned	We replaced 09no's phase carbon brush & 01 Ground carbon brush.	During service time we check & found Phase carbon brush, Ground carbon brush warn out.so we replaced all by new one.-Field Engineer-Dinesh Babu R. | Problem solved-Field Operations Manager-Devasudar Singh | closed-Phone Technical Support-Senthil M. | Closed-Functionality Support Lead-Murugesan P. | -Quality-Vijay Chinnaswamy	Carbon brush.jpg Carbon brush
CIR-10000054	100260108	EVER MELLOW ENERGY(INDIA) PVT LTD	Theni-Alagapuri	WF-IN-022-0834-Y2-A-013	0.85	65	Standard	Indar	20305001161	Gamesa(China)	601977	High Temperature	STD+	Standard	17/09/2010	402272150	18/02/2016	-0	Senthil Kannan G	1404	1425	18/02/2016 22:30:06	18/02/2016 20:30:06	8881820	39337	CONTROL SYSTEM	NACELLE INSTRUMENTATION SYSTEM	GP004895, GP005798	PHONIEX	NORMAL OPERATION	1119776427	WTG stopped due to error no:2118 Interbus error We check & found RTD module was failed indication frequently also brake thermister was open.								Grid Fluctuation,Material defective,Input voltage problem	Assigned	We check & found RTD module was failed indication frequently also brake thermister was open. We replaced RTD module and brake pad then restart the machine.	WTG stopped due to error no:2118 Interbus error We check & found RTD module was failed indication frequently also brake thermister was open. We replaced RTD module and brake pad then restart the machine. -Field Engineer-Senthil Kannan G | Closed-Field Operations Manager-Devasudar Singh | Field Alert implementation must be ensured-Phone Technical Support-Senthil M. | Based on failure rate we have check and ensure the field alert implementation status-Functionality Support Lead-Shankar Anand R. | -Quality-Vijay Chinnaswamy
CIR-10000078	100260108	EVER MELLOW ENERGY(INDIA) PVT LTD	Theni-Alagapuri	WF-IN-022-0834-Y2-A-013	0.85	65	Standard	Indar	20305001161	Gamesa(China)	601977	High Temperature	STD+	Standard	17/09/2010	402282673	26/02/2016	-0	Yukesh D.	1404	1425	26/02/2016 00:00:37	26/02/2016 22:45:37	8884970	39485	MECHANICAL	NACELLE INSTRUMENTATION SYSTEM	GP005798,GP021828	GAMESA, YUASA	NORMAL OPERATION		WTG Stopped due to error no:411 High brake temp. We check and found brake pad with thermistor open & also brake circuit battery backup Battery was failed.	Brake pad with thermistor & Battery back up 12 V battery failure.	Breakdown	SF.NO:622(Evermellow)	Grid drop,Continuous operation, Grid Fluctuations, Expired	D.Yukesh, A.Parasuraman	Brake pad with thermistor & Battery back up 12 V battery replaced	01no, o2no's	Grid drop,Continuous operation Grid Fluctuations, Expired	Assigned	We check and found brake pad with thermistor open & also brake circuit battery backup Battery was failed. We replaced all by new one.	WTG Stopped due to error no:411 High brake temp. We check and found brake pad with thermistor open & also brake circuit battery backup Battery was failed. We replaced all by new one. -Field Engineer-Yukesh D. | Solved-Field Operations Manager-Devasudar Singh | Pls ensure the DM Implementation-Phone Technical Support-Senthil M. | Please check the Battery life time from PTS and replace the battery practively. Also implement the DM - B5021301. For more info regarding DM, please contact PTS India-Functionality Support Lead-Anand A.P | -Quality-Vijay Chinnaswamy	Battery 12V.jpg
CIR-10000236	100260108	EVER MELLOW ENERGY(INDIA) PVT LTD	Theni-Alagapuri	WF-IN-022-0834-Y2-A-013	0.85	65	Standard	Indar	20305001161	Gamesa(China)	601977	High Temperature	STD+	Standard	17/09/2010	402322244	02/04/2016	-0	Devasudar Singh	1404	1440	02/04/2016 17:30:00	02/04/2016 17:00:00	8907200	40271	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP004895	PHONIEX	NORMAL OPERATION	1352058705	During service time error no:2118 Interbus error occur, so we check & found RTD module failure,	RTD module failure	Service time	SF.NO:622(EVERMELLOW)	Continuous operation, material defect	T.Stalinkumar, J.Kalimuthu, M.Vinu	we replaced RTD module by new one.	01no	Continuous operation, material defect	Assigned	we replaced RTD module by new one.	During service time error no:2118 Interbus error occur, so we check & found RTD module failure,we replaced new RTD module.mow machine running normal.-Field Engineer-Stalin Kumar T | Problem solved-Field Operations Manager-Devasudar Singh | Shield earthing must ensured-Phone Technical Support-Senthil M. | RCA to be done-Functionality Support Lead-Shankar Anand R.	IMG_20160405_063840.jpg RTD MODULE
CIR-10000071	100260109	Shiny Knitwear (P) Ltd.	Theni-Alagapuri	WF-IN-022-0834-Y2-A-009	0.85	65	Standard	Indar	20305001158	Gamesa(China)	602009	High Temperature	STD+	Standard	22/09/2010	402221871	26/02/2016	-0	Yukesh D.	1404	1425	26/02/2016 22:00:37	26/02/2016 21:00:37	7585640	39305	CONTROL SYSTEM	NACELLE INSTRUMENTATION SYSTEM	GP004262, P393462	PHONIEX, ABB	NORMAL OPERATION		WTG Stopped due to error no:206 Hydraulic group protection triggered. We Checked and found KR280 PLC relay & KM280 contactor was failure.	PLC 24V Relay & Hyd.Contactor failure	Breakdown	SF.NO:641(Shiny)	Continuos(on and off) operating, Grid Fluctuation. Grid down for long time and Fluctuat	D.Yukesh, A.Parasuraman	PLC 24V Relay & Hyd.Contactor Replaced	Each 01no	Continuos(on and off) operating, Grid Fluctuation. Grid down for long time and Fluctuation	Assigned	We Checked and found KR280 PLC relay & KM280 contactor was failure, We replaced KR280 relay & KM280 contactor and restart the turbine.	Problem solved-Field Engineer-Yukesh D. | Problem solved-Field Operations Manager-Devasudar Singh | Contractor must replaced every 3 Years-Phone Technical Support-Senthil M. | Contactor replacement frequency sent to field alert-Functionality Support Lead-Murugesan P. | -Quality-Vijay Chinnaswamy	PLC relay.jpg PLC Relay
CIR-10000077	100260109	Shiny Knitwear (P) Ltd.	Theni-Alagapuri	WF-IN-022-0834-Y2-A-009	0.85	65	Standard	Indar	20305001158	Gamesa(China)	602009	High Temperature	STD+	Standard	22/09/2010	402221871	26/02/2016	-0	Yukesh D.	1404	1425	26/02/2016 22:00:37	26/02/2016 21:00:37	7585640	39305	CONTROL SYSTEM	NACELLE INSTRUMENTATION SYSTEM	GP004262, P393462	PHONIEX, ABB	NORMAL OPERATION		WTG Stopped due to error no:206 Hydraulic group protection triggered. We Checked and found KR280 PLC relay & KM280 contactor was failure.	PLC 24V Relay & Hyd.Contactor failure	Breakdown	SF.NO:641(Shiny)	Continuos(on and off) operating, Grid Fluctuation. Grid down for long time and Fluctuat	D.Yukesh, A.Parasuraman	PLC 24V Relay & Hyd.Contactor Replaced	Each 01no	Continuos(on and off) operating, Grid Fluctuation. Grid down for long time and Fluctuation	Assigned	We Checked and found KR280 PLC relay & KM280 contactor was failure, We replaced KR280 relay & KM280 contactor and restart the turbine.	WTG Stopped due to error no:206 Hydraulic group protection triggered. We Checked and found KR280 PLC relay & KM280 contactor was failure We replaced KR280 relay & KM280 contactor and restart the turbine -Field Engineer-Yukesh D. | solved-Field Operations Manager-Devasudar Singh | to be investigated-Phone Technical Support-Senthil M. | Field Alert already sent once in 4years-Functionality Support Lead-Murugesan P. | -Quality-Vijay Chinnaswamy	PLC relay.jpg PLC Relay
CIR-10000240	100260109	Shiny Knitwear (P) Ltd.	Theni-Alagapuri	WF-IN-022-0834-Y2-A-009	0.85	65	Standard	Indar	20305001158	Gamesa(China)	602009	High Temperature	STD+	Standard	22/09/2010	402323587	05/04/2016	-0	Devasudar Singh	1404	1440	05/04/2016 17:30:00	05/04/2016 16:30:00	7605280	40146	ELECTRICAL	ELECTRICAL CABINET SYSTEM	50074, GP004898	INGETEAM, PHONIEX	NORMAL OPERATION	1113813836, 504984516	During service time error no:2118 Interbus error & error no:2250 Crowbar not ok.we check & found AO2 module failure & Crowbar card failure.	AO2 module, Crowbar card failure	During service time.	SF.NO:641(SHINY)	Continuous operation, grid drop	D.Yukesh, T.Stalinkumar, S.vijayakumar	AO2 module, Crowbar card replaced by new one.	Each 01no	Continuous operation, grid drop	Assigned	we replaced AO2 module & crowbar card by new one.	During service time error no:2118 Interbus error & error no:2250 Crowbar not ok.we check & found AO2 module failure & Crowbar card failure.we replaced all by nnew one.now machine running normal.-Field Engineer-Yukesh D. | Problem solved-Field Operations Manager-Devasudar Singh | further investigation recommended-Phone Technical Support-Senthil M. | Please check with Diag+ tool for remote analysis-Functionality Support Lead-Murugesan P. | -Functionality Support Specialist-Karthick M.	IMG_20160406_001202.jpg AO2 module | IMG_20160406_001329.jpg Crowbar card
CIR-10000103	100260126	NSP Knitting Mills	Theni-Alagapuri	WF-IN-022-0834-Y1-A-004	0.85	65	Standard	Indar	20305001176	Gamesa(China)	602066	High Temperature	STD+	Standard	20/08/2010		11/03/2016	-0	Devasudar Singh	1404	1440	11/03/2016 18:00:00	11/03/2016 17:00:00	8804050	40396	ELECTRICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	880162, REL0068, 50591, GP004262, P393462	VICKERS, FINDER, GAMESA,PHONIEX,ABB	NORMAL OPERATION		Wtg manually stopped for 66 month service work that time error no:800 Pitch Activating error occur.	Proportional valve, Hyd.contactor, top timer, PLC 24 Relay, Phase carbon brush failure	During service time	SF.NO:60(NSP)	Continuous operation	K.Sankar, G.Bala, S.Johnpeter	Proportional valve, Hyd.contactor, top timer, PLC 24 Relay, Phase carbon brush replaced all by new one.	01, 01, 01, 02no's, 09no's	Continuous operation, Grid drop, Shortcircuit	Assigned	So we check & found proportional valve problem & also find top timer, Hyd.contactor , Phase carbon brush,PLC relay failure.	Problem solved-Field Engineer-John Peter S | Problem solved-Field Operations Manager-Devasudar Singh | closed-Phone Technical Support-Senthil M. | Please implement B5041203-EN_R00 - Filter for proportional valve-Functionality Support Lead-Anand A.P | -Quality-Vijay Chinnaswamy	IMG_20160302_130116.jpg PLC relay | Carbon brush.jpg Phase carbon brush | IMG_20160312_211314.jpg Pro.Valve
CIR-10000065	100260128	Ch. V. V. subba Rao	Theni-Alagapuri	WF-IN-022-0834-Y2-A-006	0.85	65	Standard	Indar	20305001181	Gamesa(China)	602065	High Temperature	STD+	Standard	17/08/2010	402283079	24/02/2016	-0	Dinesh Babu R.	1404	1425	24/02/2016 17:45:58	24/02/2016 16:45:58	7518140	40049	MECHANICAL	NACELLE INSTRUMENTATION SYSTEM	P370104	GAMESA	NORMAL OPERATION		WTG Manually stopped for 66Month service work. That time We checked and found brake pad was failure	Brake pad	Service	SF.NO:385(SUBBARAO)	Grid Fluctuation,Material defective,Input voltage problem	R.Dineshbabu, K.Sankar, G.Bala	Brake pad 01 no replaced	01no	Grid Fluctuation,Material defective,Input voltage problem	Assigned	We checked and found brake pad was failure We replaced it by new one all then restart the machine	WTG Manually stopped for 66Month service work, that time We checked and found brake pad was failure We replaced it by new one all then restart the machine -Field Engineer-Dinesh Babu R. | Problem solved-Field Operations Manager-Devasudar Singh | consumables no need for investigation-Phone Technical Support-Senthil M. | Please implement the DM- B5021301 to avoid such brake pad thermistor failure in future-Functionality Support Lead-Anand A.P | -Quality-Vijay Chinnaswamy	Brake pad.jpg Brake pad
CIR-10000090	100260133	K.P.R. Mill Ltd	Theni-Alagapuri	WF-IN-022-0834-Y1-A-015	0.85	65	Standard	Indar	20305001195	Gamesa(China)	602079	High Temperature	STD+	Standard	20/08/2010		01/03/2016	-0	Avudaippan M	1404	1425	01/03/2016 19:00:16	01/03/2016 16:50:16	8090070	40162	CONTROL SYSTEM	NACELLE INSTRUMENTATION SYSTEM	GP004262	PHONIEX	NORMAL OPERATION		Wtg stopped due to error no:114 Low pressure on yaw brake.	Yaw PLC relay24V failure	Breakdown time	SF.NO:1004(KPR)	Due to heat, continuous operation.	K.Ramesh, M.Avudaiappan	24V PLC relay replaced	01no	Dut to heat, Continuous operation.	Assigned	We check & found PLC 24V relay failure.	Wtg stopped due to error no:114 low pressure on yaw brake. we check & found 24VPLC relay failure, so we replaced by new one, that time Yaw accmulator also precharged.-Field Engineer-Avudaippan M | Solved-Field Operations Manager-Devasudar Singh | Component level investigation to be done-Phone Technical Support-Senthil M. | We will check this relay failure is occational or repeated-Functionality Support Lead-Murugesan P. | analysis shall be done based on the Failure trend-Functionality Support Specialist-Venkatesh S | -Quality-Vijay Chinnaswamy	IMG_20160302_130116.jpg
CIR-10000102	100260133	K.P.R. Mill Ltd	Theni-Alagapuri	WF-IN-022-0834-Y1-A-015	0.85	65	Standard	Indar	20305001195	Gamesa(China)	602079	High Temperature	STD+	Standard	20/08/2010	402298269	10/03/2016	-0	Yukesh D.	1404	1425	10/03/2016 18:00:00	10/03/2016 17:00:00	8093700	40332	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP004262, 50591, 50592	PHONIEX, GAMESA	NORMAL OPERATION		Wtg manually stopped for 66 month service work that time we found Yaw 24vPLC relay & Phase carbon brush & Ground carbon brush failure.	PLC relayfailure & Phase & Ground carbon brush war out	Service time	SF.NO:1004(KPR mills)	Conitinuous operation, Grid drop	D.Yukesh, A.Parasuraman, G.Bala	All materials replaced bynnew one.	01no, 15no's, 01no	Continuous operation, Grid drop	Assigned	We replaced PLC replay & Carbon brush by new one.	Problem solved-Field Engineer-Yukesh D. | Problem Solved-Field Operations Manager-Devasudar Singh | Brush Survival Hours to be measured based on Consumption details- Closed-Phone Technical Support-Senthil M. | If it is preventive maintance CIR not required-Functionality Support Lead-Murugesan P. | -Quality-Vijay Chinnaswamy	IMG_20160302_130116.jpg PLC relay | Carbon brush.jpg Carbon brush
CIR-10000479	100260320	Sri Shanmugavel Mills (P) Ltd.	PETHAPPAMPATTI	WF-IN-022-0853-Y1-A-003	0.85	65	Standard	Gamesa wind Tianjin, China	801001021	Gamesa(Spain)	100054	High Temperature	STD+	Standard	31/03/2011	402342905	25/04/2016	-0	Karuppusamy K.	1402	1439	25/05/2016 10:20:00	25/04/2016 08:15:00	8091760	41206	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP002750	semikran	GRID FAILURE		After grid drop WTG stopped due to 3210-Skip Error rotor inverter phase-2								rotor internal failure	Applied	while checking the related connections and we found that rotor skip 2 module was failure so we replaced new one	WTG restarted normally -Field Engineer-Karuppusamy K. | -Field Operations Manager-Sureshkumar K
CIR-10000483	100260259	Sri Shanmugavel Mills (P) Ltd.	PETHAPPAMPATTI	WF-IN-022-0853-Y1-A-010	0.85	65	Standard	Gamesa wind Tianjin, China	801000938	Gamesa(China)	602323	High Temperature	STD+	Standard	31/03/2011	402353139	05/05/2016	-0	Sakthivel D.	1402	1439	05/05/2016 18:40:00	05/05/2016 17:30:00	7788870	41370	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP019699	ABB	NORMAL OPERATION		WTG stopped due to 3404-Conf. preload contact error occurred								contactor failure	Applied		WTG restarted normally -Field Engineer-Sakthivel D. | -Field Operations Manager-Sureshkumar K
CIR-10000633	100260398	Sivaraj Spinning Mills (P) Limited	PETHAPPAMPATTI	WF-IN-022-0853-Y1-A-008	0.85	65	Standard	Gamesa wind Tianjin, China	447575	Gamesa(China)	602440	High Temperature	STD+	Standard	31/03/2011	402342906	25/04/2016	-0	Vellingiri R.	1402	1439	25/04/2016 20:27:57	25/04/2016 20:27:57	7805800	69856	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP004897	Phoenix	NORMAL OPERATION		WTG stopped due to 2118-Bus error inter bus fail								module failure	Applied	while checking plc shows 3.16 so we changed the AI module new one	WTG restarted normally -Field Engineer-Vellingiri R. | -Field Operations Manager-Sureshkumar K
CIR-10000637	100260373	Devendran Coal International Private Limited	PETHAPPAMPATTI	WF-IN-022-0853-Y1-A-014	0.85	65	Standard	Gamesa wind Tianjin, China	801001093	Rexroth	72802022131	High Temperature	STD+	Standard	31/03/2011	402366365	19/05/2016	-0	Sorna Raja G.	1402	1439	19/04/2016 06:05:00	19/05/2016 04:05:00	8864760	40291	CONTROL SYSTEM	ELECTRICAL CABINET SYSTEM	GP004896	PHOENIX	NORMAL OPERATION	1114462392	WTG stopped due to 2118 - Bus Error Interbus Fail error								RS-485 module	Applied	we checked the PLC shows 3.15 so weconfirm RS485 failure we change that new one .	WTG restarted normally -Field Engineer-Sorna Raja G. | -Field Operations Manager-Sureshkumar K
CIR-10000302	100260309	Havukal Tea & Produce Company Pvt Limited	PETHAPPAMPATTI	WF-IN-022-0853-Y3-A-001	0.85	65	Standard	Gamesa wind Tianjin, China	801001029	Gamesa(Spain)	400870	High Temperature	STD+	Standard	31/03/2011	402331454	13/04/2016	-0	Vellingiri R.	1402	1439	13/04/2016 17:00:00	13/04/2016 14:05:00	6797880	39906	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP095799 & REL0068	FINDER	NORMAL OPERATION		WTG stopped due to 3230-Time out peried DC-link error								circuit board was proplem	Assigned	While checking we found chopper card got failure so it was replaced with new one	WTG restarted normally-Field Engineer-Vellingiri R. | Brake chopper PCB was replaced-Field Operations Manager-Sureshkumar K | Assign to FSL-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.
CIR-10000076	100260159	Chenduran Cotspin (India) Pvt. Ltd	Theni-Alagapuri	WF-IN-022-0834-Y2-A-003	0.85	65	Standard	Indar	20305001183	Gamesa(Spain)	300038	High Temperature	STD+	Standard	17/08/2010	402283133	25/02/2016	216-High number of start-ups in hydr unit	Senthil Kannan G	1404	1425	25/02/2016 17:00:36	25/02/2016 16:30:36	8064580	39822	MECHANICAL	HYDRAULIC SYSTEM AND PITCH CONTROL	109882, 50050,REL0068	OILEAR, GAMESA, FINDER	NORMAL OPERATION		WTG Manually stopped for 66 Month service work. While we check & found brake accumulator & Top timer,Encoder coupler was failure.	Brake accmulator, Encoder coupler, top timer was failure.	During service time	SF.NO:346(CHENDURAN)	Material problem,Frequent Brake. Grid Fluctuation, No of operation High	K.Sankar, G.Senthilkannan, T.Stalinkumar	Brake accmulator, Encoder coupler, top timer was replaced	Each 01 no	Material problem,Frequent Brake. Grid Fluctuation, No of operation High	Assigned	While we check & found brake accumulator & Top timer, Encoder coupler was failure . We replaced by new one and restart the WTG	WTG Manually stopped for 66 Month service work. While we check & found brake accumulator & Top timer was failure . We replaced by new one and restart the WTG. -Field Engineer-Senthil Kannan G | Problem solved-Field Operations Manager-Devasudar Singh | Further RCA extended-Phone Technical Support-Senthil M. | Failure rate to be analysed-Functionality Support Lead-Shankar Anand R. | -Quality-Vijay Chinnaswamy	20160204_170509.jpg | IMG_20160226_092925.jpg
CIR-10000372	100260118	Chenduran Cotspin (India) Pvt. Ltd	Theni-Alagapuri	WF-IN-022-0834-Y1-A-007	0.85	65	Standard	Indar	20305001174	Gamesa(China)	602054	High Temperature	STD+	Standard	18/08/2010	402356529	07/05/2016	-0	Kalimuthu J	1404	1440	07/05/2016 12:00:00	07/05/2016 10:00:00	9166300	41600	ELECTRICAL	ELECTRICAL CABINET SYSTEM	GP008132	INGITEAM	LIGHTNING	433525837	Wtg stopped due to error no:3409 Line protection tripped. we check & found Grid MPCB FG001, Dhen guard was failed & also Multiplexer card failure.	Multiplexer card failure	breakdown	SF.NO:254(Chenduran)	Heavy lightening	K.Ramesh, J.Kalimuthu, T.Stalinkumar, M.Vinu	we replaced multiplexer card by new one.	01no	Heavy lightening	Assigned	we replaced multiplexer card, Grid MPCB by new one.	Wtg stopped due to error no:3409 Line protection tripped. we check & found Grid MPCB FG001, Dhen guard was failed & also Multiplexer card failure.we replaced all by new one.-Field Engineer-Kalimuthu J | Problem solved-Field Operations Manager-Devasudar Singh | Surge control action to be taken at BOP level-Phone Technical Support-Senthil M. | -Functionality Support Lead-Murugesan P.	IMG_20160509_230232.jpg Multiplexer card
CIR-10000058	100260122	Ch. V. V. subba Rao	Theni-Alagapuri	WF-IN-022-0834-Y2-A-012	0.85	65	Standard	Indar	20305001173	Gamesa(China)	602052	High Temperature	STD+	Standard	17/08/2010		19/02/2016	-0	Yukesh D.	1404	1425	19/02/2016 17:30:05	19/02/2016 17:00:05	9099290	39980	CONTROL SYSTEM	NACELLE INSTRUMENTATION SYSTEM	REL0068	FINDER	NORMAL OPERATION		Wtg Manually stopped for 66Month service work. During service time Interbus error occur , so we check and found PLC display it shows 3.0 error & also we check top timer was Failure.								Material problem,Loose connection Due to Heat,Grid Fluctuation	Assigned	During service time Interbus error occur , so we check and found PLC display it shows 3.0 error & also we check top timer was Failure. We replaced it by new one and restarted the turbine.	Wtg Manually stopped for 66Month service work. During service time Interbus error occur , so we check and found PLC display it shows 3.0 error & also we check top timer was Failure. We replaced it by new one and restarted the turbine. -Field Engineer-Yukesh D. | Problem solved-Field Operations Manager-Devasudar Singh | Maintenance process to be verified-Phone Technical Support-Senthil M. | Based on failure rate the RCA to be carried out-Functionality Support Lead-Shankar Anand R. | -Quality-Vijay Chinnaswamy